## Slide 1: Heritage House CA2300541 Mendocino County Jar Test
by Guy Schott, P.E.
September 17, 2019

## Slide 2: Dark Gulch Creek

## Slide 3: Source Water: Dark Gulch Creek
Source Water Characteristics
Turbidity: 1.25 NTU
pH: 7.53
UVT: 75.0%, UVA: 0.125/cm
0.4 um Filtered
UVT: 75.6%, UVA: 0.121/cm

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Coagulant Used for Jar Testing
7066 (Garratt Callahan)
10 – 30% Poly Aluminum Hydroxychloride Sulfate
SG = 1.2
7032 (Garratt Callahan)
50% ACH (Aluminum Chlorohydrate)
50% H2O
SG = 1.34

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.53
LCA #1:
7066: 101 mg/L as product
(no pH adjustment)
Final pH: 6.78
LCA #2:
7032: 27.2 mg/L as product
(no pH adjustment)
Final pH: 7.32

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Filtrate and %UVT/UVA Analysis
For this study, all jars were samples for Filtrate and %UVT/UVA analysis immediately at the end of the flocculation period.

## Slide 9: Heritage House: Jar Test 1-8 Results
Jar | 200 RPM Flash Mix sec | 30 RPM Floc Mix min | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 60 | 5 | 90 | 0.07 | 94.1 | 0.026 | 78.5 | 0.18
J2 | 60 | 5 | 95 | 0.07 | 94.3 | 0.025 | 79.3 | 0.17
J3 | 60 | 5 | 100 | 0.06 | 94.6 | 0.024 | 80.2 | 0.21
J4 | 60 | 5 | 105 | 0.05 | 94.8 | 0.023 | 81.0 | 0.20
J5 | 0 | 5 | 90 | 0.06 | 93.7 | 0.028 | 76.9 | 0.31
J6 | 0 | 5 | 95 | 0.05 | 93.9 | 0.027 | 77.7 | 0.27
J7 | 0 | 5 | 100 | 0.05 | 94.1 | 0.026 | 78.5 | 0.31
J8 | 0 | 5 | 105 | 0.06 | 94.0 | 0.027 | 77.7 | 0.31

## Slide 10: Heritage House: Jar Test 9-15 Results
Jar | 200 RPM Flash Mix sec | 30 RPM Floc Mix min | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 60 | 5 | 24.0 | 0.25 | 89.9 | 0.046 | 62.0 | 0.90
J10 | 60 | 5 | 25.5 | 0.09 | 91.5 | 0.039 | 67.8 | 0.97
J11 | 60 | 5 | 27.0 | 0.21 | 90.6 | 0.043 | 64.5 | 1.18
J12 | 60 | 5 | 28.5 | 0.08 | 92.5 | 0.034 | 71.9 | 0.90
J13 | 0 | 5 | 28.5 | 0.25 | 90.5 | 0.043 | 64.5 | 0.91
J14 | 0 | 5 | 30.0 | 0.20 | 91.0 | 0.041 | 66.1 | 0.81
J15 | 0 | 5 | 31.5 | 0.20 | 91.4 | 0.039 | 67.8 | 1.05

## Slide 11: Jars 1-4 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 12: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
90 mg/L 7066
Filtrate 0.07 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction: 78.5%
Settled: 0.18 NTU
95 mg/L 7066
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 79.3%
Settled: 0.17 NTU
100 mg/L 7066
Filtrate 0.06 NTU
UVT: 94.6%
UVA: 0.024/cm
UVA Reduction: 80.2%
Settled: 0.21 NTU
105 mg/L 7066
Filtrate 0.05 NTU
UVT: 94.8%
UVA: 0.023/cm
UVA Reduction: 81%
Settled: 0.20 NTU

## Slide 13: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.

## Slide 14: Visual of Filterability of Jars 1-4

## Slide 15: Jars 5-8 Test No Flash Mix Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 16: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
90 mg/L 7066
Filtrate 0.06 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 76.9%
Settled: 0.31 NTU
95 mg/L 7066
Filtrate 0.05 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 77.7%
Settled: 0.27 NTU
100 mg/L 7066
Filtrate 0.05 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction: 78.5%
Settled: 0.31 NTU
105 mg/L 7066
Filtrate 0.06 NTU
UVT: 94.0%
UVA: 0.027/cm
UVA Reduction: 77.7%
Settled: 0.31 NTU

## Slide 17: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.

## Slide 18: Visual of Filterability of Jars 5-8

## Slide 19: Jars 9-12 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7032

## Slide 20: Jars 9-12: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
24 mg/L 7032
Filtrate 0.25 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction: 62%
Settled: 0.90 NTU
25.5 mg/L 7032
Filtrate 0.09 NTU
UVT: 91.5%
UVA: 0.039/cm
UVA Reduction: 67.8%
Settled: 0.97 NTU
27 mg/L 7032
Filtrate 0.21 NTU
UVT: 90.6%
UVA: 0.043/cm
UVA Reduction: 64.5%
Settled: 1.18 NTU
28.5 mg/L 7032
Filtrate 0.08 NTU
UVT: 92.5%
UVA: 0.034/cm
UVA Reduction: 71.9%
Settled: 0.90 NTU

## Slide 21: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.

## Slide 22: Visual of Filterability of Jars 9-12

## Slide 23: Jars 13-15 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7032

## Slide 24: Jars 13-15: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
28.5 mg/L 7032
Filtrate 0.25 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction: 64.5%
Settled: 0.91 NTU
30 mg/L 7032
Filtrate 0.20 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction: 66.1%
Settled: 0.81 NTU
31.5 mg/L 7032
Filtrate 0.20 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction: 67.8%
Settled: 1.05 NTU

## Slide 25: Jars 13-15: After 25-minutes of settling, settled water turbidity is taken.

## Slide 26: Visual of Filterability of Jars 13-15

## Slide 27: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate). For this study, sample was taken immediately at the end of flocculation process.
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 28: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 29: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 30: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 31: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 32: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732