## Slide 1: Howell Mountain Mutual Water Company CA2810001 Napa County Jar Test
by Guy Schott, P.E.
October 3, 2019

## Slide 2: Source Waters (blend): Lake Henne/Lake Newton
Source Water Characteristics
October 3, 2019
Turbidity: 1.16 NTU
pH: 7.39
UVT: 73.7%, UVA: 0.133/cm
0.4 um Filtered
UVT: 74.8%, UVA: 0.126/cm

## Slide 3: UVT/UVA
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Applied Coagulants for Jar Testing
Pro Pac 917 (NTU Technologies, Inc.)
10% Trade Secret
40-50% Aluminum Chlorohydrate (ACH)
40-50% Water
SG = 1.25-1.34

## Slide 5: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.39
LCA #1:
917: 18.8 mg/L as product (no pH adjustment)
Final pH: 7.20

## Slide 6: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 7: Howell Mountain MWC: Jar Test Results Flash Mix 200 RPM for 30 Seconds
Jar | RPM Floc Mix 5 min | NaOCl mg/L | 917 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min | Cl2 Residual mg/L
J1 | 30 | 0.0 | 24 | 0.08 | 89.6 | 0.048 | 0.22 | 0
J2 | 30 | 0.5 | 24 | 0.08 | 89.9 | 0.046 | 0.36 | 0
J3 | 30 | 1.0 | 24 | 0.07 | 90.0 | 0.046 | 0.32 | 0
J4 | 30 | 1.5 | 24 | 0.06 | 90.3 | 0.044 | 0.33 | 0
J5 | 30 | 0.0 | 24 | 0.08 | 89.4 | 0.049 | 0.31 | 0
J6 | 30 | 1.5 | 24 | 0.07 | 90.2 | 0.045 | 0.22 | 0
J7 | 30 | 2.0 | 24 | 0.06 | 90.2 | 0.045 | 0.33 | 0
J8 | 30 | 2.5 | 24 | 0.06 | 90.3 | 0.044 | 0.26 | 0.09
J9 | 30 | 1.5 | 24 | 0.05 | 90.7 | 0.042 | - | 0

## Slide 8: Howell Mountain MWC: Jar Test 10-11 Results Flash Mix 200 RPM (30 sec), Floc Mix 30 RPM (5 min), Data After 200 mL Lab Filtration (1.2 um Isopore)
Jar | 917 mg/L | Elapses Time Hrs. | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Post Filter NaOCl mg/L | Cl2 Residual mg/L
10 | 24 | 0 | 0.06 | 89.6 | 0.048 | 0 | -
10 | - | 2.5 | 0.06 | 89.8 | 0.047 | 0 | -
10 | - | 7.5 | 0.06 | 89.4 | 0.049 | 0 | -
11 | 24 | 0 | 0.06 | 89.5 | 0.048 | - | -
11 | - | 0.1 | 0.08 | 91.1 | 0.040 | 2.0 | 0.98
11 | - | 2.5 | 0.08 | 91.9 | 0.037 | - | 0.45
11 | - | 7.5 | 0.08 | 91.9 | 0.037 | - | 0.21

## Slide 9: Howell Mountain MWC: Jar Test 12 Results Flash Mix 200 RPM (30 sec), Floc Mix 30 RPM (5 min), Data After 200 mL Lab Filtration (1.2 um Isopore)
Jar | 917 mg/L | Elapses Time Hrs. | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Post Filter NaOCl mg/L | Cl2 Residual mg/L
J12 | 24 | 0 | 0.07 | 90.3 | 0.044 | 0 | -
J12 | - | 0 | 0.07 | 91.2 | 0.040 | 2.0 | 1.1
J12 | - | 0.5 | 0.07 | 91.8 | 0.037 | - | 0.76
J12 | - | 1.0 | 0.08 | 91.9 | 0.037 | - | 0.67
J12 | - | 1.5 | 0.08 | 92.2 | 0.035 | - | 0.59
J12 | - | 2.9 | 0.08 | 92.0 | 0.036 | - | 0.41
J12 | - | 7.5 | 0.08 | 92.2 | 0.035 | - | 0.26
J12 | - | 25 | 0.07 | 91.9 | 0.037 | - | 0

## Slide 10: Howell Mountain MWC: Jar Test 13 Results Flash Mix 200 RPM (30 sec), Floc Mix 30 RPM (5 min), Data After 200 mL Lab Filtration (1.2 um Isopore)
Jar | Pre- NaOCl mg/L | 917 mg/L | Elapses Time Hrs. | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Post Filter NaOCl mg/L | Cl2 Residual mg/L
13 | 0 | 24 | 0 | 0.06 | 90.3 | 0.044 | 0 | -
13 | - | - | 0 | 0.08 | 91.4 | 0.040 | 2.0 | 0.96
13 | - | - | 0.5 | 0.08 | 92.4 | 0.037 | - | 0.59
13 | - | - | 1.1 | 0.08 | 92.4 | 0.037 | - | 0.48
13 | - | - | 4.6 | 0.08 | 93.0 | 0.035 | - | 0.21

## Slide 11: Howell Mountain MWC: Jar Test 14 Results Flash Mix 200 RPM (30 sec), Floc Mix 30 RPM (5 min), Data After 200 mL Lab Filtration (1.2 um Isopore)
Jar | Pre- NaOCl mg/L | 917 mg/L | Elapses Time Hrs. | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Post Filter NaOCl mg/L | Cl2 Residual mg/L
14 | 1.5 | 24 | 0 | 0.05 | 90.8 | 0.042 | - | 0.05
14 | - | - | 0 | 0.07 | 91.1 | 0.040 | 2.0 | 1.33
14 | - | - | 0.5 | 0.09 | 91.7 | 0.038 | - | 1.15
14 | - | - | 1.1 | 0.09 | 92.0 | 0.036 | - | 1.04
14 | - | - | 4.6 | 0.10 | 92.2 | 0.035 | - | 0.71

## Slide 12: Jars 1-4 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 917

## Slide 13: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
NaOCl = 0.0 mg/L
24 mg/L 917
Filtrate 0.08 NTU
UVT: 89.6%
UVA: 0.048/cm
Settled: 0.22 NTU
NaOCl = 0.5 mg/L
24 mg/L 917
Filtrate 0.08 NTU
UVT: 89.9%
UVA: 0.046/cm
Settled: 0.36 NTU
NaOCl = 1.0 mg/L
24 mg/L 917
Filtrate 0.07 NTU
UVT: 90.0%
UVA: 0.046/cm
Settled: 0.32 NTU
NaOCl = 1.5 mg/L
24 mg/L 917
Filtrate 0.06 NTU
UVT: 90.3%
UVA: 0.044/cm
Settled: 0.33 NTU

## Slide 14: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 15: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
NaOCl = 0.0 mg/L
24 mg/L 917
Filtrate 0.08 NTU
UVT: 89.6%
UVA: 0.048/cm
Settled: 0.22 NTU
NaOCl = 0.5 mg/L
24 mg/L 917
Filtrate 0.08 NTU
UVT: 89.9%
UVA: 0.046/cm
Settled: 0.36 NTU
NaOCl = 1.0 mg/L
24 mg/L 917
Filtrate 0.07 NTU
UVT: 90.0%
UVA: 0.046/cm
Settled: 0.32 NTU
NaOCl = 1.5 mg/L
24 mg/L 917
Filtrate 0.06 NTU
UVT: 90.3%
UVA: 0.044/cm
Settled: 0.33 NTU

## Slide 16: Visual of Filterability of Jars 1-4
NaOCl = 0.0 mg/L
24 mg/L 917
Filtrate 0.08 NTU
UVT: 89.6%
UVA: 0.048/cm
Settled: 0.22 NTU
NaOCl = 0.5 mg/L
24 mg/L 917
Filtrate 0.08 NTU
UVT: 89.9%
UVA: 0.046/cm
Settled: 0.36 NTU
NaOCl = 1.0 mg/L
24 mg/L 917
Filtrate 0.07 NTU
UVT: 90.0%
UVA: 0.046/cm
Settled: 0.32 NTU
NaOCl = 1.5 mg/L
24 mg/L 917
Filtrate 0.06 NTU
UVT: 90.3%
UVA: 0.044/cm
Settled: 0.33 NTU

## Slide 17: Jars 5-8 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 917

## Slide 18: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
NaOCl = 0.0 mg/L
24 mg/L 917
Filtrate 0.08 NTU
UVT: 89.4%
UVA: 0.049/cm
Settled: 0.31 NTU
NaOCl = =1.5 mg/L
24 mg/L 917
Filtrate 0.07 NTU
UVT: 90.2%
UVA: 0.045/cm
Settled: 0.22 NTU
NaOCl = =2.0 mg/L
24 mg/L 917
Filtrate 0.06 NTU
UVT: 90.2%
UVA: 0.045/cm
Settled: 0.33 NTU
NaOCl = =2.5 mg/L
24 mg/L 917
Filtrate 0.06 NTU
UVT: 90.3%
UVA: 0.044/cm
Settled: 0.26 NTU

## Slide 19: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 20: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
NaOCl = 0.0 mg/L
24 mg/L 917
Filtrate 0.08 NTU
UVT: 89.4%
UVA: 0.049/cm
Settled: 0.31 NTU
NaOCl = =1.5 mg/L
24 mg/L 917
Filtrate 0.07 NTU
UVT: 90.2%
UVA: 0.045/cm
Settled: 0.22 NTU
NaOCl = =2.0 mg/L
24 mg/L 917
Filtrate 0.06 NTU
UVT: 90.2%
UVA: 0.045/cm
Settled: 0.33 NTU
NaOCl = =2.5 mg/L
24 mg/L 917
Filtrate 0.06 NTU
UVT: 90.3%
UVA: 0.044/cm
Settled: 0.26 NTU

## Slide 21: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 22: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 23: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 24: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 25: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 26: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732