## Slide 1: Garberville Sanitary District CA1210008 Tracer Study February 4, 2019
Tracer Study:
Reactor: Pressure Vessel
Volume: 20,000 Gallons
Diameter: 10 ft
Length: 36 ft
Baffled Tank (over/under)
Inlet/Outlet Full Perforated Baffles
Performed by:
Guy Schott, P.E.
CA Division of Drinking Water

## Slide 2: Table of Content
Summary of Tracer Results
Reactor Design
Tracer Sample Locations
Graph 1: Modified Step-Dose Curve
Graph 2: Normalized Modified Step-Dose Curve to F-Curve
Purpose of a Tracer Test
Disinfection Exposure Time of Fluid in Vessel for Determining Ct10
Ct10 Value
Baffling Factor (BF)
Tracer Test Method
Method of Analysis and Equipment

## Slide 3: Garberville SD Tracer Test Results
Modified Step-Dose
Test Date: 2/4/19
Baffling Factor (t10/HRT): 0.54
Average Flow: 204 gpm
HRT: 98 minutes
t10: 53 minutes
Tracer: Fluoride (2.55 mg/L)
Inlet Sample Frequency:
  5 gallon bucket (fill duration 4 -5 min)
  12 samples (6 – 59 min range)
Outlet Sample Frequency:
  0 – 40 min (4 min)
  40 – 69 min (1 min)

## Slide 4
Horizontal Pressure Clearwell Design
The inlet baffled holes were plugged off except the 12 holes within the highlighted boundary.

## Slide 5: Inlet Tracer Sample Location
The applied tracer dosage is determined by grab sampling downstream of the tracer injection point before the tank inlet. Sample water is allowed to flow into a 5 gallon bucket for 4-5 minutes then sample is taken from bucket. This provides an average tracer dosage concentration. Samples are taken throughout the tracer study.

## Slide 6: Outlet Tracer Sample Location
Samples are taken from the outlet to determine the time it takes for 10% of the applied tracer dosage to exit the tank. Sample frequency is increased in the time range of the expected 10% dosage mass.
Sample Frequency for this test:
0 – 40 minutes (4 minute intervals)
40 – 69 minutes ( 1 minute intervals)

## Slide 7: Garberville SD – Modified Step-Dose Curve
Chart: Step-Dose Curve
| 0 | 4 | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0135 | 0.053 | 0.058 | 0.064 | 0.083 | 0.098 | 0.11 | 0.121 | 0.137 | 0.149 | 0.174 | 0.191 | 0.207 | 0.224 | 0.237 | 0.255 | 0.271 | 0.314 | 0.361 | 0.406 | 0.442 | 0.471 | 0.51
Dosage: 2.64 mg/L
0.26 mg/L at t10
t10: 53 min
HRT: 98 min
t10/HRT = 0.54

## Slide 8: Garberville SD – Modified Step-Dose Curve Normalized to F-Curve
Chart: Normalized F-Curve
| 0 | 4.07E-2 | 8.14E-2 | 0.12209999999999999 | 0.1628 | 0.20349999999999999 | 0.24419999999999997 | 0.28489999999999999 | 0.3256 | 0.36629999999999996 | 0.40699999999999997 | 0.41717499999999996 | 0.42734999999999995 | 0.437525 | 0.44769999999999999 | 0.45787499999999998 | 0.46804999999999997 | 0.47822499999999996 | 0.48839999999999995 | 0.49857499999999999 | 0.50874999999999992 | 0.51892499999999997 | 0.52910000000000001 | 0.53927499999999995 | 0.54944999999999999 | 0.55962499999999993 | 0.56979999999999997 | 0.57997499999999991 | 0.59014999999999995 | 0.600325 | 0.61049999999999993
 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0051136 | 0.020076 | 0.02197 | 0.024242 | 0.031439 | 0.037121 | 0.041667 | 0.045833 | 0.051894 | 0.056439 | 0.065909 | 0.072348 | 0.078409 | 0.084848 | 0.089773 | 0.096591 | 0.10265 | 0.11894 | 0.13674 | 0.15379 | 0.16742 | 0.17841 | 0.19318
t10/HRT = 0.54

## Slide 9: Purpose of a Tracer Study
To determine the hydraulic efficiency or disinfectant exposure time of water through one or more reactors.
The addition of known quantities of a nonreactive chemical (tracer) is added in the form of a pulse (slug) or step-input.
The time of travel or disinfectant exposure time through the reactor is related to:
  Flow rate
  Reactor water volume
  Water Depth
  Reactor configuration

## Slide 10: Disinfection Exposure Time of Fluid in Vessel for Determining Ct10
“C” is the disinfectant residual (mg/L) at the point of inactivation compliance.
The disinfection exposure time of water used for Ct10 calculation is the time (t10) it takes for 10 percent of the water entering the reactor to exit the reactor.
To determine this, a marker (nonreactive tracer) is introduced into the water and is monitored leaving the reactor.
Example: 1.0 Kg of tracer is slug-dose; t10 is that time when 0.1 Kg of tracer material (10%) has exit the reactor.

## Slide 11: Ct10 Value
- Log inactivation is based on the Delivered Dose, “Ct10”
  “C” is the disinfectant residual (mg/L)
  “t10” is the exposure or contact time (minutes)
  Multiply them:
C • t10 = mg/L • min (delivered dose)
The calculated Ct10 value is looked up in EPA Ct tables to determine the log inactivation based on specific monitoring parameters (pH, disinfectant residual and/or temperature).

## Slide 12: Baffling Factor (BF)
Baffling factor or short-circuiting factor:
  Determined from tracer study or estimated
  BF = t10/ HRT from tracer study
  HRT (hydraulic residence time) = reactor volume divided by reactor flow
Once the BF is determined, then it is applied to the operations of the reactor for determining the disinfectant exposure time.
Example:
  Clearwell operating volume: 20,000 gallons
  Exit flow: 200 gpm
  BF: 0.50, from tracer study
  Calculated contact or disinfection exposure time:
    20,000 gal ÷ 200 gpm × 0.50 = 50 minutes = t10

## Slide 13: Test Method
Modified Step-Dose Method
It is a continue feed of tracer at constant rate and plant flow throughout the duration of the test. The “Step-Dose” test is run to 3-4 HRT to achieve reactor outlet steady-state tracer concentration. The time “t10” is determined when 10% of the tracer dose concentration has exist the reactor. The “Modified Step-Dose” test allows the test to be completed in less than 1 HRT by physical measurements of the tracer inlet flow concentration to verify dosage.

## Slide 14: Method of Analysis and Equipment
Intellical™ ISEF121 Fluoride (F-) Ion Selective Electrode (ISE)
HQ40d Portable ISE Multi-Parameter Meter
Fluoride Ionic Strength Adjustor (ISA)
Fluoride Standards (0.2/2.0 & 0.5/ 5.0 mg/L)
50 mL graduated cylinder
Finnpipette F2 variable volume pipette, capacity 0.5 - 5 mL
Electrode stirrer stand
50 mL beakers
Stir Bar, Magnetic, Polygon

## Slide 15: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Guy.Schott@waterboards.ca.gov
707-576-2732