## Slide 1: Konocti Harbor Resort & Spa CA1710016 Lake County Jar Test
by Guy Schott, P.E.
September 16, 2020

## Slide 2: Konocti Harbor Resort & Spa Source Water Characteristics September 16, 2020
Source
Turbidity: 9.5 NTU
pH: 8.14
UVT: 80.9%, UVA: 0.091/cm
0.4 um Filtered
Turbidity: 0.55 NTU
UVT: 83.9%, UVA: 0.076/cm

## Slide 3: Konocti Harbor Resort & Spa Source Water Sept 16, 2020
Source
pH: 8.14
Turbidity: 9.5 NTU
UVT: 80.9%,
UVA: 0.091/cm
0.4 um Filtered
Turbidity: 0.55 NTU
UVT: 83.9%,
UVA: 0.076/cm
Coagulant Dose:
9810: 30 mg/L
Post Media Filtration:
0.13 NTU
UVT: 89.1%,
UVA: 0.049/cm
UVA Reduction: 35.5%
Post GAC Filtration:
0.12 NTU
UVT: 91.4%,
UVA: 0.038/cm
UVA Reduction: 50%

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Coagulant Used for Jar Testing
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate (ACH)
45-50% Water
5% Proprietary
SG = 1.25 – 1.34

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 8.14
LCA #1:
9810: 27.5 mg/L as product
pH adjusted to 7.5 with Acetic Acid

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Konocti Harbor Resort Spa, Source: Clear Lake Jar Test 1-4 Results, Flash Mix 200 RPM (20 sec)
Jar # | 20 RPM Floc Mix (min) | NaOCl mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 5 | 0 | 26 | 0.14 | 88.8 | 0.051 | 32.9 | 0.47
J2 | 5 | 0 | 28 | 0.13 | 88.6 | 0.052 | 31.6 | 0.52
J3 | 5 | 0 | 30 | 0.11 | 88.8 | 0.051 | 32.9 | 0.56
J4 | 5 | 0 | 32 | 0.11 | 88.6 | 0.052 | 31.6 | 0.35

## Slide 9: Konocti Harbor Resort Spa, Source: Clear Lake Jar Test 5-12 Results, Flash Mix 200 RPM (20 sec)
Jar # | 20 RPM Floc Mix (min) | NaOCl mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J5 | 5 | 2.5 | 26 | 0.11 | 88.4 | 0.053 | 30.3 | 0.41
J6 | 5 | 2.5 | 28 | 0.13 | 88.5 | 0.053 | 30.3 | 0.42
J7 | 5 | 2.5 | 30 | 0.09 | 88.7 | 0.051 | 32.9 | 0.44
J8 | 5 | 2.5 | 32 | 0.08 | 88.6 | 0.052 | 31.6 | 0.28
J9 | 5 | 4.0 | 26 | 0.08 | 90.7 | 0.042 | 44.7 | 0.39
J10 | 5 | 4.0 | 28 | 0.09 | 90.7 | 0.042 | 44.7 | 0.28
J11 | 5 | 4.0 | 30 | 0.08 | 91.0 | 0.040 | 47.4 | 0.38
J12 | 5 | 4.0 | 32 | 0.09 | 90.9 | 0.041 | 46.1 | 0.30

## Slide 10: Filterability
Jars 1-16, 25 mL was syringed 5 minutes after the end of flocculation period.
Jars 17-20, 25 mL was syringed immediately at the end of flocculation period.

## Slide 11: Konocti Harbor Resort Spa, Source: Clear Lake Jar Test 13-20 Results, Flash Mix 200 RPM (20 sec), NaOCl Dose: 5.0 mg/L, 9810: 30 mg/L
Jar # | Floc 20 RPM min | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 5 min | Settle NTU 10 min | Settle NTU 25 min
J13 | 5 | 0.08 | 90.8 | 0.041 | 46.1 | n/a | 0.74 | 0.35
J14 | 15 | 0.09 | 90.9 | 0.041 | 46.1 | n/a | 0.37 | 0.30
J15 | 30 | 0.08 | 91.6 | 0.038 | 50.0 | n/a | 0.27 | 0.29
J16 | 45 | 0.07 | 91.1 | 0.040 | 47.4 | n/a | 0.16 | 0.20
J17 | 5 | 0.09 | 91.4 | 0.039 | 48.7 | 0.45 | 0.50 | 0.36
J18 | 15 | 0.08 | 91.1 | 0.040 | 47.4 | 0.36 | 0.29 | 0.32
J19 | 30 | 0.07 | 91.3 | 0.039 | 48.7 | 0.33 | 0.31 | 0.27
J20 | 45 | 0.08 | 91.4 | 0.038 | 50.0 | 0.16 | 0.23 | 0.25

## Slide 12: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9810

## Slide 13: Jars 1-4: End of 5-minute flocculation (20 RPM) duration.
26 mg/L 9810
Filtrate 0.14 NTU
UVT: 88.8%
UVA: 0.051/cm
UVA Reduction 32.9%
Settled: 0.47 NTU
28 mg/L 9810
Filtrate 0.13 NTU
UVT: 88.6%
UVA: 0.052/cm
UVA Reduction 31.6%
Settled: 0.52 NTU
30 mg/L 9810
Filtrate 0.11 NTU
UVT: 88.8%
UVA: 0.051/cm
UVA Reduction 32.9%
Settled: 0.56 NTU
32 mg/L 9810
Filtrate 0.11 NTU
UVT: 88.6%
UVA: 0.052/cm
UVA Reduction 31.6%
Settled: 0.35 NTU

## Slide 14: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 15: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
26 mg/L 9810
Filtrate 0.14 NTU
UVT: 88.8%
UVA: 0.051/cm
UVA Reduction 32.9%
Settled: 0.47 NTU
28 mg/L 9810
Filtrate 0.13 NTU
UVT: 88.6%
UVA: 0.052/cm
UVA Reduction 31.6%
Settled: 0.52 NTU
30 mg/L 9810
Filtrate 0.11 NTU
UVT: 88.8%
UVA: 0.051/cm
UVA Reduction 32.9%
Settled: 0.56 NTU
32 mg/L 9810
Filtrate 0.11 NTU
UVT: 88.6%
UVA: 0.052/cm
UVA Reduction 31.6%
Settled: 0.35 NTU

## Slide 16: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Pre-Oxidation (NaOCl) Applied Coagulant 9810

## Slide 17: Jars 5-8: End of 5-minute flocculation (20 RPM) duration.
2.5 mg/L NaOCl
26 mg/L 9810
Filtrate 0.11 NTU
UVT: 88.4%
UVA: 0.053/cm
UVA Reduction 30.3%
Settled: 0.41 NTU
2.5 mg/L NaOCl
28 mg/L 9810
Filtrate 0.13 NTU
UVT: 88.5%
UVA: 0.053/cm
UVA Reduction 30.3%
Settled: 0.42 NTU
2.5 mg/L NaOCl
30 mg/L 9810
Filtrate 0.09 NTU
UVT: 88.7%
UVA: 0.051/cm
UVA Reduction 32.9%
Settled: 0.44 NTU
2.5 mg/L NaOCl
32 mg/L 9810
Filtrate 0.08 NTU
UVT: 88.6%
UVA: 0.052/cm
UVA Reduction 31.6%
Settled: 0.28 NTU

## Slide 18: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 19: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
2.5 mg/L NaOCl
26 mg/L 9810
Filtrate 0.11 NTU
UVT: 88.4%
UVA: 0.053/cm
UVA Reduction 30.3%
Settled: 0.41 NTU
2.5 mg/L NaOCl
28 mg/L 9810
Filtrate 0.13 NTU
UVT: 88.5%
UVA: 0.053/cm
UVA Reduction 30.3%
Settled: 0.42 NTU
2.5 mg/L NaOCl
30 mg/L 9810
Filtrate 0.09 NTU
UVT: 88.7%
UVA: 0.051/cm
UVA Reduction 32.9%
Settled: 0.44 NTU
2.5 mg/L NaOCl
32 mg/L 9810
Filtrate 0.08 NTU
UVT: 88.6%
UVA: 0.052/cm
UVA Reduction 31.6%
Settled: 0.28 NTU

## Slide 20: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Pre-Oxidation (NaOCl) Applied Coagulant 9810

## Slide 21: Jars 9-12: End of 5-minute flocculation (20 RPM) duration.
4.0 mg/L NaOCl
26 mg/L 9810
Filtrate 0.08 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 44.7%
Settled: 0.39 NTU
4.0 mg/L NaOCl
28 mg/L 9810
Filtrate 0.09 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 44.7%
Settled: 0.28 NTU
4.0 mg/L NaOCl
30 mg/L 9810
Filtrate 0.08 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 47.4%
Settled: 0.38 NTU
4.0 mg/L NaOCl
32 mg/L 9810
Filtrate 0.09 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 46.1%
Settled: 0.30 NTU

## Slide 22: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 23: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
4.0 mg/L NaOCl
26 mg/L 9810
Filtrate 0.08 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 44.7%
Settled: 0.39 NTU
4.0 mg/L NaOCl
28 mg/L 9810
Filtrate 0.09 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 44.7%
Settled: 0.28 NTU
4.0 mg/L NaOCl
30 mg/L 9810
Filtrate 0.08 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 47.4%
Settled: 0.38 NTU
4.0 mg/L NaOCl
32 mg/L 9810
Filtrate 0.09 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 46.1%
Settled: 0.30 NTU

## Slide 24: No Photos Shown Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5/15/30/45 min (20 RPM) Pre-Oxidation (NaOCl) Applied Coagulant 9810

## Slide 25: No Photos Shown Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5/15/30/45 min (20 RPM) Pre-Oxidation (NaOCl) Applied Coagulant 9810

## Slide 26: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed to 20 - 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 27: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 28: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 29: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 30: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 31: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732