## Quarterly Summary Rpt Template
RB-Assigned SSO ID No. | RB-Assigned Tracking No. | RB-entered Reporting Agency | RB-entered Responsible Agency | RB-entered Start Date | RB-entered End Date | RB-entered Total Volume | RB-entered Recovered Volume | RB-entered Cause - Short Description | Tracking No. | Regional Board Contact Notified (Name, or "VOICE MAIL", or "FAX") | Date & Time Reported | Reported By | Phone No. | Reporting Agency | Responsible Agency | Start Date & Time | End Date & Time | Estimated Overflow Flow Rate (gallons per minute) | Total Overflow Volume (Gallons) | Overflow Volume Recovered (Gallons) | Overflow Volume Released to Environment (Gallons) | SSO Location -- Street Address | SSO Location -- City | SSO Zip Code | SSO County (SD, RV, OR) | SSO Structure I.D. | No. of Overflows within 1000 ft. of this location in past 12 months | Dates of Overflows within 1000 ft. of this location in past 12 months | SSO Cause (Short Description) | SSO Cause (Detailed Description) | SSO Correction and Prevention | 72-hour period measurable precipitation? (Y or N) | Entered Storm Drain? (Y or N) | Reached surface waters other than storm drain? (Y or N) | Initial Receiving Waters | Secondary Receiving Waters | Final Sewage Destination | Local Health Services Agency Notified (Y or N) | OES Notified (Y or N) | Warning Signs Posted (Y or N) | Location of Posting | No. of Days Signs Posted | Remarks | RB staff review comments | Place an "X" here if this is definitely a private spill | Place an "P", "R", "S", "O" here if it is a Plant, Recycled, Secondary, or Other non SSO
|  | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-07-01 12:45 | 2003-07-01 13:45 | 40 | 0 | Blockage | 034001 | Quarterly Report |  | Mike Shope | (760)725-9762 | MCB, CAMP PENDLETON | MCB, CAMP PENDLETON | 07/01/03 12:45 | 07/01/03 13:45 | 0.666 | 40 | 0 | 40 | BLDG. 62537, Building 62537 | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 12Y30 Line Type: Clay Line Size: 8 Inch | 0 |  | Blockage | Marines cleaning barracks, flushed paper towels down the drian causing blockage. | CORRECTIVE: Ram jetted with root cutter. Pumper truck required due to low GPM. PREVENTATIVE: FMD is working on a contract to foam the mainlines on base where root problems occur. Contract is not in place at this time. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Concrete sidewalk. | N | N | N | None | 0 | Remarks: Location flowed through: From manhole 120 feet down concrete swale/sidewalk.. Total distance traveled: 120 Feet. Expected public contact: No
|  | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-08-08 15:15 | 2003-08-08 17:30 | 675 | 675 | Roots | 034002 | Quarterly Report |  | Mike Shope | (760)725-9763 | MCB, CAMP PENDLETON | MCB, CAMP PENDLETON | 08/08/03 15:15 | 08/08/03 17:30 | 5 | 675 | 675 | 0 | Manhole 11Y51, Building 52540 | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 11Y51 overflow. Line Type: VCP Line Size: 6 | 1 | 02/03/03 | Roots | Line blocked with roots and rocks. | CORRECTIVE: Used pumper truck to pump down manhole, jetted line to clear blockage. Used pumper truck to clean up ponded sewage and recover roots from line. PREVENTATIVE: Continued preventative maintenance of sewer lines. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Asphalt parking area | N | N | Y | None | 0 | Remarks: Location flowed through: From manhole spill traveled 375' south across asphalt parking lot and ponded. All ponded sewage recovered.. Total distance traveled: 375 feet. Expected public contact: No
|  | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-08-26 11:00 | 2003-08-26 14:45 | 2250 | 0 | Grease | 034003 | Brian Kelley, (858)467-4254 | 2003-08-27 09:09 | Mike Shope | (760)725-9764 | MCB, CAMP PENDLETON | MCB, CAMP PENDLETON | 08/26/03 11:00 | 08/26/03 14:45 | 10 | 2250 | 0 | 2250 | Rear loading dock, Building 22186 | MCB, CAMP PENDLETON | 92055-5008 | SD | Cleanout to Blg 22186 Clay Line Size: 8 | 1 | 04/17/03 | Grease | Grease blockage in the main line caused when a contractor mistakenly placed a steam blow down line into a grease trap. The steam emulsified the grease and sent it downstream where it collected and caused spill. | CORRECTIVE: Pumper trucks were used to jet the line and clear the blockage. Steam blow down line was moved from grease trap and routed to sewage manhole. PREVENTATIVE: Boiler operators will inspect the blow down line for correct placement. | N | Y | N | None | None | Overflow did not reach actual receiving waters but: Vegetated earthen storm drainage channel | Y | Y | N | None | 0 | Remarks: Spill travelled 40 ft NW over pavement to street, 150 ft SW along curving gutter to storm drain inlet, 35 ft NW through storm drain culvert underneath road, then 200 ft in vegetated earthen storm drainage channel
|  | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-09-22 08:45 | 2003-09-22 09:45 | 100 | 95 | Roots | 034004 | Brian Kelley, (858)467-4254 | 2003-09-22 16:05 | Mike Shope | (760)725-9765 | MCB, CAMP PENDLETON | MCB, CAMP PENDLETON | 09/22/03 8:45 | 09/22/03 9:45 | 1.67 | 100 | 95 | 5 | Area 53, Building 53427 | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 10Y23 Line Type: VCP Line Size: 8 | 0 |  | Roots | The spill was indirectly caused by a contractor cleaning the sewerlines. A rootball apparently was forced into a lateral where it was hidden from cleaning crew. Eventually flow through the lateral forced the debris back into the mainline. | CORRECTIVE: Contractor cleared blockage with jetter and vacuum truck. PREVENTATIVE: Contractor will continue cleaning and televising sewer lines. | N | Y | N | None | None | Overflow did not reach actual receiving waters but: Concrete swale. | N | N | N | None | 0 | Remarks: Spill traveled 2 ft east across grass then 65 ft northeast down sidewalk to asphalt. Spill continued 105 ft northwest, then 50 ft northeast on asphalt, then 130 ft northwest to concrete swale then 440 ft northeast in the swale.
|  | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-10-06 09:45 | 2003-10-06 10:15 | 150 | 30 | Roots | 34005 | Quarterly Report |  | Mike Shope | (760)725-9762 | MCB, CAMP PENDLETON | MCB, CAMP PENDLETON | 2003-10-06 09:45 | 2003-10-06 10:15 | 5 | 150 | 30 | 120 | Deluz Housing, Building 14519A | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 1-Y-187 Line Type: VCP Line Size: 8 | 0 |  | Roots | Tree roots caused partial blockage in the 8 inch VCP sewer line. | CORRECTIVE: The sewer line was jetted with a pumper truck to clear the roots. PREVENTATIVE: The trees are scheduled to be cut in the area of the spill. A root cutter will also be used to help prevent a reoccurrence of blockage. | N | N | N | None | None | Overflow did not reach actual receiving waters but percolated in vegatated earthen area. | Y | N | Y | Deluz Housing, Building 14519A | 3 | Remarks: Spill traveled from manhole down dirt road 200 feet northwest where it stopped and percolated. Second spill path traveled west 85 feet then north over embankment 50 feet where it mixed with first spill path.
|  | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-10-08 07:30 | 2003-10-08 09:10 | 700 | 0 | Roots | 34006 | Quarterly Report |  | Mike Shope | (760)725-9762 | MCB, CAMP PENDLETON | MCB, CAMP PENDLETON | 2003-10-08 07:30 | 2003-10-08 09:10 | 7 | 700 | 0 | 700 | Deluz Housing, Building 14519A | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 1-Y-187 Line Type: VCP Line Size: 8 | 1 | 2003-10-06 | Roots | Tree roots caused partial blockage in the 8 inch VCP sewer line. | CORRECTIVE: The sewer line was jetted with a pumper truck. PREVENTATIVE: The trees are scheduled to be cut down in the area of the spill. A root cutter will also be used to clean out the roots in the pipe to prevent another reoccurrence of blockage. | N | N | N | None | None | Overflow did not reach actual receiving waters but percolated in vegatated earthen area. | Y | N | Y | Deluz Housing, Building 14519A | 3 | Remarks: Spill traveled from manhole down dirt road 200 feet northwest where it stopped and percolated. Second portion of spill traveled west 85 feet then north over embankment 50 feet where it intersected the first spill path.
|  | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-11-04 07:30 | 2003-11-07 07:30 | 81100 | 0 | Line Break | 34007 | Brian Kelley, (858)467-4254 | 2003-11-07 02:50 | Mike Shope | (760)725-9762 | MCB, CAMP PENDLETON | MCB, CAMP PENDLETON | 2003-11-04 07:30 | 2003-11-07 07:30 | 0 | 81100 | 0 | 81100 | Los Flores, 41 Area | MCB, CAMP PENDLETON | 92055-5008 | SD | Force Main Line Type: PVC Line Size: 8 | 0 |  | Line Break | The 8-inch PVC Force Main line failed. Spill was intermittent with the lift station cycling on and off. | CORRECTIVE: Secured lift station 41300 to stop flow through line. Pumper trucks on site to pump down lift station. Installed new section of pipe. PREVENTATIVE: Force main will be patrolled as part of system PM. | N | N | Y | Las Flores (dry creek bed) | Pacific Ocean | Overflow did not reach actual receiving waters but spill percolated into the ground. | Y | Y | N | None | 0 | Remarks: From breakage 185 ft northeast and left dirt road, 70 ft down ravine to natural drainage, 805 ft northwest and percolated into ground. Total distance traveled: 1060 ft. Expected public contact: No
|  | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-11-14 09:00 | 2003-11-14 14:45 | 13000 | 0 | Line Break | 34008 | Brian Kelley, (858)467-4254 | 2003-11-14 16:00 | Mike Shope | (760)725-9762 | MCB, CAMP PENDLETON | MCB, CAMP PENDLETON | 2003-11-14 09:00 | 2003-11-14 02:45 | 37.68 | 13000 | 0 | 13000 | Los Flores, 41 Area | MCB, CAMP PENDLETON | 92055-5008 | SD | Force Main Line Type: PVC Line Size: 8 | 1 | 2003-11-07 | LineBreak | A section of PVC force main was exposed to the environment due to erosion. Exposure to ultraviolet radiation may have caused the PVC to become weak, which resulted in a linear 2-3 foot split in the pipe. | CORRECTIVE: The pumping station which feeds the force main was secured. The damaged 4 foot pipe section was replaced. PREVENTATIVE: Engineered backfill will be used to cover the exposed line and correct erosion points in the area. | N | N | Y | Las Flores (dry creek bed) | Pacific Ocean | Overflow did not reach actual receiving waters but spill percolated into the ground. | Y | Y | N | None | 0 | Remarks: Spill flowed from the split force main 1500 feet west through the ravine tributary where it percolated into sandy earthen area.. Total distance traveled: 1500 feet. Expected public contact: No
|  | Rancho California Water District | Rancho California Water District | 10/04/03 0820 | 10/04/03 1026 | 700 | 0 | Vandalism | 034001 | Chiara Clemente | 10/06/03 0745 | David Holguin | 909-296-6900 | Rancho California Water District | Rancho California Water District | 10/04/03 0820 | 10/04/03 1026 | 5 | 700 | 0 | 700 | 24323 Jackson Ave. | Murrieta | 92562 | RV | Construction Manhole #4 | 0 | None | Vandalism | Manhole cover was removed and large rocks and debris were dropped into manhole | Lockable covers were installed in this area | N | N | N | NA | NA | Natural low spot in dirt | N | N | Y | Affected area | 7 | N
|  | City of San Diego | City of San Diego | 2003-07-08 08:30 | 2002-07-08 08:45 | 105 | 100 | GREASE | 363454 | Fax (858) 571-6972 (RWQCB) | 2003-07-08 12:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-07-08 08:30 | 2002-07-08 08:45 | 7 | 105 | 100 | 5 | 4715 Univesity Avenue | San Diego | 92105 | SD | 6" V.C. | 1 | 10/20/2002 | GREASE | Heavy grease and rags caused stoppage. | Rodded to clear stoppage flushed to clean main and vactor to recover spill. Main needs to be added in a more frequent maintenance program due to grease released in sewer main by consumers. | N | Y | N | None | None | Dissipated in storm drain conveyance system | Y | Y | N |  | 0 | Spill was found when flusher unit was ready to start working in a sewer maintenance book. Spill was contained inmediately and supervisor notified.
|  | City of San Diego | City of San Diego | 2003-07-09 20:40 | 2003-07-09 22:55 | 3375 | 500 | ROOTS | 363778 | Fax (858) 571-6972 (RWQCB) | 2003-09-10 10:20 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-07-09 20:40 | 2003-07-09 22:55 | 25 | 3375 | 500 | 2875 | 12739 FUTURA ST. | San Diego | 92130 | SD | 8" PVC | 0 |  | ROOTS | HEAVY ROOTS IN MH 178 AND DOWNSTREAM MAIN. | VACTORED AT STORMDRAIN. RODDED AND CLEANED MH 178 TO RELIEVE BLOCKAGE. REFER TO HAVE MAINS AND MANHOLES ON EASEMENT TO BE INSPECTED AND CLEANED. TELEVISE BLOCKAGE SECTION. | N | Y | Y | CARMEL VALLEY CREEK | SOLEDAD CREEK | N/A | Y | Y | Y | Bay/Lagoon/Beach | 1 | Per the DEH we posted signs at Torrey Pines on July 10, 2003 after testing signs were removed on July 11, 2003
|  | City of San Diego | City of San Diego | 2003-07-12 14:54 | 2003-07-12 15:40 | 92 | 0 | GREASE | 364169 | Fax (858) 571-6972 (RWQCB) | 2003-07-12 17:20 | D.A. BRANCO | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-07-12 14:54 | 2003-07-12 15:40 | 2 | 92 | 0 | 92 | 4777 BAYARD ST | San Diego | 92109 | SD | 8"VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY HEAVY GREASE & RAGS | MACHINE RODDED TO RELIEVE STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-07-15 18:04 | 2003-07-15 19:05 | 305 | 0 | ROOTS | 364577 | Fax (858) 571-6972 (RWQCB) | 2003-07-15 20:00 | C. MICKELSON | (858) 654-4130 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-07-15 18:04 | 2003-07-15 19:05 | 5 | 305 | 0 | 305 | 8303 SUGARMAN DR. | San Diego | 92037 | SD | 8" VC | 0 |  | ROOTS | ROOTS GROWING IN CITY SEWER MAIN. | FLUSHED TO RELEIVE BLOCKAGE. CLEANED 2 SECTIONS UP AND 2 SECTIONS DOWN, TOTAL 5 SECTIONS. REFER TO BE TELEVISED. | N | N | N | None | None | SOAKED INTO HILLSIDE BEHIND 8303 SUGARMAN DR. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-07-16 10:50 | 2003-07-16 13:40 | 1275 | 1225 | ROOTS | 364683 | Fax (858) 571-6972 (RWQCB) | 2003-07-16 15:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-07-16 10:50 | 2003-07-16 13:40 | 7.5 | 1275 | 1225 | 50 | 4914 54th. Street | San Diego | 92115 | SD | 8" V.C. | 0 | 0 | ROOTS | Heavy roots cause spill | Flushed to clear stoppage. Vactor spill next to storm drain to prevent getting into channel. Will refer to area supervisor to televise, and to submit for possible root inhibitor treatment. Also to be added in a more frequent maintenance program. | N | Y | N | None | None | Dissipated in storm drain conveyance system | N | Y | N |  | 0 | Spill was contained at 11:15. manhole was runing intermitently. Vactor sewege out of manhole to flush and clear main
|  | City of San Diego | City of San Diego | 2003-08-05 17:33 | 2003-08-05 22:52 | 102 | 25 | FLOOD DAMAGE | 367437 | Fax (858) 571-6972 (RWQCB) | 2003-08-06 11:30 | Jeff Wilder | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-08-05 17:33 | 2003-08-05 22:52 | 3 | 102 | 25 | 77 | 3470 Landis St. | San Diego | 92104 | SD | 8"VC | 1 | 1-7-2003 | FLOOD DAMAGE | main break on 8' VC main | Rodded to relieve stop, removed new rocks, referred to construction for repairs, Vacuumed to recover approx. 25 gal. from storm drain | N | Y | N | None | None | dissipated in storm drain | N | Y | N |  |  | Overflow was coming up though the street, containment by berming around down stream manhole and opening it.
|  | City of San Diego | City of San Diego | 2003-08-05 17:25 | 2003-08-05 18:15 | 626650 | 2000 | PUMP STATION FAILURE | 367436 | Fax (858) 571-6972 (RWQCB) | 2003-08-11 17:30 | C. MICKELSON | (858) 654-4130 | City of San Diego MWWD/O & M | City of San Diego MWWD/O & M | 2003-08-05 17:25 | 2003-08-05 18:15 | 12533 | 626650 | 2000 | 624650 | Sorrento Valley Blvd. and Sorrento Valley Rd. | San Diego | 92130 | SD | 84" VC | 0 | N/A | PUMP STATION FAILURE | Pump Station failure caused 84" overflow main to spill. | Manually ran pumps to stop spill. Cleaned and deodorized street. | N | Y | Y | Penasquitos Lagoon | Pacific Ocean |  | Y | Y | Y | Bay/Lagoon/Beach | 4
|  | City of San Diego | City of San Diego | 2003-08-09 09:34 | 2003-08-09 10:36 | 31 | 0 | ROOTS | 368167 | Fax (858) 571-6972 (RWQCB) | 2003-08-09 13:45 | D.A. BRANCO | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-08-09 09:34 | 2003-08-09 10:36 | 0.5 | 31 | 0 | 31 | 3622 KEMPER ST | San Diego | 92110 | SD | 8"VC | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS & GREASE | FLUSHED LINE TO RELIEVE STOP; CLEANED AREA; REFERRED TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-08-15 20:57 | 2003-08-15 22:00 | 315 | 0 | ROOTS | 369090 | Fax (858) 571-6972 (RWQCB) | 2003-08-15 23:35 | D.A. BRANCO | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-08-15 20:57 | 2003-08-15 22:00 | 5 | 315 | 0 | 315 | FRIARS RD & MISSION CENTER RD | San Diego | 92108 | SD | 8" CI | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | FLUSHED LINE TO RELIEVE STOP CAUSED BY ROOTS; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | SOAKED INTO CANYON AREA. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-08-18 11:30 | 2003-08-18 15:30 | 120 | 100 | OTHER | 369199 | Fax (858) 571-6972 (RWQCB) | 2003-08-19 08:00 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-08-18 11:30 | 2003-08-18 15:30 | 0.5 | 120 | 100 | 20 | 1402 K St. | San Diego | 92101 | SD | 6" VC | 0 | 0 | OTHER | The overflow was due to a built in sag in the main due to a 33" water main running on top of sewer. | Main is in CIP process. | N | Y | N | None | None | Dissipated into storm drain | Y | Y | N |  | 0 | Main stoppage caused 731-I with moderate damage with 731-out of cleanout. Area Supv will refer to be televised.
|  | City of San Diego | City of San Diego | 2003-08-22 08:39 | 2003-08-22 13:20 | 126.45 | 0 | ROOTS | 369795 | Fax (858) 571-6972 (RWQCB) | 2003-08-22 14:30 | Ernest Vasquez | (858) 614-5719 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-08-22 08:39 | 2003-08-22 13:20 | 0.45 | 126.45 | 0 | 126.45 | 5447 Maisel Way | San Diego | 92115 | SD | 8" V. C. | 0 | 0 | ROOTS | Heavy roots. | Machine & hand rodded to releive the stoppage. Will be refered to T.V. section to televise main, also to area supervisor for further recommendations. | N | N | N | None | None | Dissipated in canyon area. | Y | Y | N |  | 0 | This section needs to be referred to be root foamed depending on what T.V. finds.
|  | City of San Diego | City of San Diego | 2003-09-02 16:30 | 2003-09-03 06:00 | 72900 | 22750 | ROCKS | 371194 | Fax (858) 571-6972 (RWQCB) | 2003-09-05 15:10 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-09-02 16:30 | 2003-09-03 06:00 | 90 | 72900 | 22750 | 50150 | 33RD ST. X BROADWAY | San Diego | 92102 | SD | 8"vc Main | 0 |  | ROCKS | ROCKS AND DEBRIS IN EASEMENT SEWER MAIN. | VACTORED STORM DRAIN SYSTEM TO CONTAIN AND RECOVER SEWAGE. RODDED AND FLUSHED MAIN TO RESTORE FLOW AND REMOVE ROCKS AND DEBRIS FROM SEWER SYSTEM. WILL TELEVISE MAIN TO CHECK FOR PIPE INTEGRITY. | N | Y | Y | Chollas Creek | San Diego Bay |  | Y | Y | Y | Bay/Lagoon/Beach | 2 | Signs were picked up and this is the final report.
|  | City of San Diego | City of San Diego | 2003-09-03 12:42 | 2003-09-03 12:56 | 280 | 0 | CONSTRUCTION | 371279 | Fax (858) 571-6972 (RWQCB) | 2003-09-03 15:10 | Ernest Vasquez | (858) 614-5719 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-09-03 12:42 | 2003-09-03 12:56 | 20 | 280 | 0 | 280 | Crownhill & Solidad Mtn. Rd. | San Diego | 92037 | SD | 8" V.C. | 0 | 0 | CONSTRUCTION | Sludge & Rags | Refer to area supervisor for futher action. | N | N | N | None | None | Dissapated before it reached any storm drains. | Y | Y | N |  | 0 | Overflow dissapated before it reached any storm drains or interceptor.
|  | City of San Diego | City of San Diego | 2003-09-03 16:30 | 2003-09-03 19:00 | 150 | 0 | ROOTS | 371393 | Fax (858) 571-6972 (RWQCB) | 2003-09-03 21:00 | JOHNNY PEAY | (858) 654-4133 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-09-03 16:30 | 2003-09-03 19:00 | 1 | 150 | 0 | 150 | OLYMPIC PL. X OLYMPIC ST. | San Diego | 92105 | SD | 8" VC | 0 |  | ROOTS | ROOTS GROWING IN CITY SEWER MAIN COLLECTING GREASE. | HAND RODDED MAIN TO RELEIVE BLOCKAGE. WILL CLEAN TOMORROW WITH MACHINE RODDER. REFER TO HAVE MAIN TELEVISED. | N | N | N | None | None | SOAKED INTO DIRT AROUND OVERFLOWING MANHOLE. | N | Y | N
|  | City of San Diego | City of San Diego | 2003-09-11 15:18 | 2003-09-11 16:40 | 2050 | 400 | FLOOD DAMAGE | 372524 | Fax (858) 571-6972 (RWQCB) | 2003-09-18 08:18 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-09-11 15:18 | 2003-09-11 16:40 | 25 | 2050 | 400 | 1650 | 2920 CLAIREMONT DR. | San Diego | 92117 | SD | 8" VC | 1 | 09/21/2002 | FLOOD DAMAGE | Stoppage in city caused stoppage in private lateral | VACTORED OVERFLOW. FLUSHED AND RODDED MAIN TO RESTORE FLOW. TELEVISED MAIN, CONFIRMING MAIN BREAK. WILL MAKE MAIN REPAIR IN AM. | N | N | N | None | None | DRIED IN DIRT 20' WEST OF APARTMENT PARKING LOT. | N | Y | N |  |  | Upon further investigation this spill was caused by a blockage in the city main , which resulted in a private lateral. The spill caused flodding in side the resident..
|  | City of San Diego | City of San Diego | 2003-09-16 07:44 | 2003-09-16 10:05 | 3666 | 3600 | ROCKS | 373125 | Fax (858) 571-6972 (RWQCB) | 2003-09-16 13:15 | Marcelino Oregel | (619) 614-5719 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-09-16 07:44 | 2003-09-16 10:05 | 26 | 3666 | 3600 | 66 | Erma Road and Scripps Ranch Blvd. | San Diego | 92131 | SD | 10" V. C. | 0 | 0 | ROCKS | Large rock and light grease causes stoppage. | Flushed mains, and referred to area supervisor for routine cleaning maintenance, and to be televised. | N | Y | N | None | None | Dissipated in storm drain conveyed system | Y | Y | N |  | 0 | Overflow was contained at 8:45, and area was cleaned inmediately.
|  | City of San Diego | City of San Diego | 2003-09-19 08:05 | 2003-09-19 08:50 | 5.4 | 0 | ROOTS | 373810 | Fax (858) 571-6972 (RWQCB) | 2003-09-19 12:00 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-09-19 08:05 | 2003-09-19 08:50 | 0.12 | 5.4 | 0 | 5.4 | 4835 Lomitas Drive | San Diego | 92116 | SD | 6" V. C. | 0 | 0 | ROOTS | Roots and a piece of V. C. material cause overflow. | Flushed main to relieve stoppage. Vactored spill next to manhole to prevent to get into storm drain channel. Referred to T.V. crews and to area supervisor for further evaluation. | N | N | N | None | None | Dissipated in the sidewalk gutter | Y | Y | N |  | 0 | Call for a T. V. crew to televise main. House Flooding and Damage report filed on 4830 Lomitas Dr.
|  | City of San Diego | City of San Diego | 2003-09-27 09:20 | 2003-09-27 10:07 | 235 | 100 | GREASE | 375297 | Fax (858) 571-6972 (RWQCB) | 2003-09-27 13:25 | D.A. BRANCO | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-09-27 09:20 | 2003-09-27 10:07 | 5 | 235 | 100 | 135 | 2254 52ND ST | San Diego | 92105 | SD | 6"VC | 1 | 10-20-2002 | GREASE | BLOCKAGE CAUSED BY HEAVY GREASE. | FLUSHED LINE TO RELIEVE STOP; VACUUM SEWAGE IN CURB & CLEAN AREA; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DEISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-10-04 10:21 | 2003-10-04 11:29 | 17 | 0 | ROOTS | 376589 | Fax (858) 571-6972 (RWQCB) | 2003-10-04 15:05 | D.A. BRANCO | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-10-04 10:21 | 2003-10-04 11:29 | 0.25 | 17 | 0 | 17 | 2205 WILLOW ST | San Diego | 92106 | SD | 6"CP | 0 | 0 | ROOTS | Blockage was caused by roots. | Flushed line to relieve stop; refer to area supervisor for further evaluation. | N | N | N | None | None | DRIED IN STREET | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-10-09 07:51 | 2003-10-09 08:25 | 850 | 600 | BLOCKAGE | 377417 | Fax (858) 571-6972 (RWQCB) | 2003-10-13 07:50 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-10-09 07:51 | 2003-10-09 08:25 | 25 | 850 | 600 | 250 | 4600 Collwood, Blv | San Diego | 92105 | SD | 12 VC | 0 |  | BLOCKAGE | Main had roots due to extensive amount of trees which were planted in area | Rodded main to relieve the stoppage, flushed main two up and two down for city protection, will refer to area supervisor. | N | Y | N | None | None | Disapated in storm drain | Y | Y | N |  |  | Flushed main two sections up and down for city protection.Will generate finale report when bacti reports are in. Bacti samples came back on 10-10-03.Per county health no signs needed to be posted.
|  | City of San Diego | City of San Diego | 2003-10-13 06:30 | 2003-10-13 07:30 | 9 | 0 | OTHER | 379259 | Fax (858) 571-6972 (RWQCB) | 2003-01-03 13:20 | John Eifling | (619) 428-7014 | City of San Diego MWWD/O&M | City of San Diego MWWD/O&M | 2003-10-13 06:30 | 2003-10-13 07:30 | 0.15 | 9 | 0 | 9 | Dairy Mart Rd. | San Diego | 92173 | SD | Valve,Sldg.Line | 0 | 0 | OTHER | Leak on 2" valve on blended sludge line | Repaired 2" pvc valve | N | N | Y | Tiajuana River | None | Dried in river bed | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-10-13 14:30 | 2003-10-13 14:45 | 1995 | 1495 | OTHER | 379293 | Fax (858) 571-6972 (RWQCB) | 2003-10-13 16:00 | Joe Cordova | (619) 221-8728 | City of San Diego MWWD/O&M | City of San Diego MWWD/O&M | 2003-10-13 14:30 | 2003-10-13 14:45 | 133 | 1995 | 1495 | 500 | 1902 Gatchell Rd. | San Diego | 92106 | SD | Bypass Pump | 0 | o | OTHER | Contractors bypass pump at Point Loma Treatment Plant | Contractor will install isolation valves on bypass | N | y | y | Pacific Ocean | None | None | Y | Y | N |  | 0
|  | City of San Diego | City of San Diego | 2003-10-14 14:30 | 2003-10-14 15:15 | 180 | 0 | OTHER | 378309 | Fax (858) 571-6972 (RWQCB) | 2003-10-17 13:40 | Lester Finch | (858) 614-4577 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-10-14 14:30 | 2003-10-14 15:15 | 4 | 180 | 0 | 180 | 2750 Bayside Walk | San Diego | 92109 | SD | Air Valve | 0 |  | OTHER | Air valve didn't seal properly and caused a small leak on air valve when the force main was in operation. | Shut the air valve off at main to stop the leak, and the air valve is being replaced. In addtion to being placed on a Maint schedule. | N | N | N | None | None | Soaked into the ground and disapated | N | Y | N |  |  | Small amount of sewage discharged from the air valve when the force main was in operation. Visual estimate of approximately 180 gal spilled and soaked into ground. Per the S.D. County Dept/ of Envirormental Health no sign posting were required.
|  | City of San Diego | City of San Diego | 2003-10-14 18:30 | 2003-10-14 20:00 | 10080 | 0 | FLOOD DAMAGE | 378198 | Fax (858) 571-6972 (RWQCB) | 2003-10-23 17:30 | Jeff Wilder | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-10-14 18:30 | 2003-10-14 20:00 | 112 | 10080 | 0 | 10080 | 2656 BAYSIDE WALK | San Diego | 92109 | SD | 12' PVC | 2 | 12/3/2002, 5/20/03 | FLOOD DAMAGE | FORCED MAIN C/O (PIGGING) CAP CAME OFF. | REROUTED SEWER FLOW TO ALTERNATE FORCED MAIN SO REPAIRS CAN BE MADE. | N | N | Y | MISSION BAY | PACIFIC OCEAN |  | Y | Y | Y |  | 7 | MH FSN AND MH ID ARE FOR FORCED MAIN C/O NUMBERS. BUILT SAND BURM ON BEACH AND DEODORIZED SAND. WILL REMOVE CONTAMINATED SAND IN AM. Picked up signs on 10/21/03 per County Health.
|  | City of San Diego | City of San Diego | 2003-10-17 01:45 | 2003-10-17 13:30 | 49966 | 49916 | CONSTRUCTION | 379262 | Fax (858) 571-6972 (RWQCB) | 2003-10-17 08:45 | Rim Stanley | (619) 692-4929 | City of San Diego MWWD/O&M | City of San Diego MWWD/O&M | 2003-10-17 01:45 | 2003-10-17 13:30 | 83 | 49966 | 49916 | 50 | 4077 N. Harbor Dr. | San Diego | 92101 | SD | Dresser Coupling | 0 | 0 | CONSTRUCTION | Dresser Coupling on force main | Replaced dersser coupling, removed soil | N | N | N | None | None | None | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-10-24 14:28 | 2003-10-24 18:30 | 1210 | 0 | GREASE | 379664 | Fax (858) 571-6972 (RWQCB) | 2003-10-24 21:25 | D.A. BRANCO | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-10-24 14:28 | 2003-10-24 18:30 | 5 | 1210 | 0 | 1210 | 1010 W. SAN YSIDRO BLVD | San Diego | 92154 | SD | 10"VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | MACHINE RODDED TO RELIEVE STOP CAUSED BY HEAVY GREASE. UNIT 718 CLEANED AREA AFFECTED BY 7-31 C/O. REFERRED TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM | N | Y | N
|  | City of San Diego | City of San Diego | 2003-10-25 16:18 | 2003-10-25 18:45 | 73.5 | 0 | CONSTRUCTION | 379821 | Fax (858) 571-6972 (RWQCB) | 2003-10-26 07:30 | Rick Donahue | (858) 654-4155 | City of San Diego MWWD/WWC | City of San Diego MWWD/O & M | 2003-10-25 16:18 | 2003-10-25 18:45 | 0.5 | 73.5 | 0 | 73.5 | 2300 Dairy Mart Rd | San Diego | 92154 | SD | 4" Air valve | 0 | 0 | CONSTRUCTION | Debirs in 4" air valve on 30" DI force main | Closed air valve, cleaned air valve. Checked, inspected and returned to service. Cleaned area. | N | N | Y | None | None | Dried on hillside next to concrete pad | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-10-28 08:30 | 2003-10-28 09:25 | 65 | 53 | ROOTS | 379933 | Fax (858) 571-6972 (RWQCB) | 2003-10-28 11:30 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-10-28 08:30 | 2003-10-28 09:25 | 1 | 65 | 53 | 12 | 3124 Carnegie.Ct | San Diego | 92122 | SD | Main | 0 |  | ROOTS | Heavy roots over growth in manhole | Rodded the main to relieve the stoppage and flushed for city protection.Called out a construction crew to conduct a confine space entry to clean the manhole for city protection . | N | Y | N | None | None | Disapated in the storm drain. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-10-29 12:10 | 2003-10-29 12:30 | 20 | 13 | ROOTS | 380047 | Fax (858) 571-6972 (RWQCB) | 2003-10-30 09:45 | Terrell Powell | (858) 614-4133 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-10-29 12:10 | 2003-10-29 12:30 | 1 | 20 | 13 | 7 | 3304 View.Place | San Diego | 92115 | SD | Main | 0 |  | ROOTS | Roots in main | Flushed the main to relieve the blockage for city protection. | N | N | N | None | None |  | Y | Y | N |  |  | Crew was working in this area and noticed the spill , that's how they responded so fast..
|  | City of San Diego | City of San Diego | 2003-10-30 17:35 | 2003-10-30 18:00 | 25 | 0 | ROOTS | 380285 | Fax (858) 571-6972 (RWQCB) | 2003-10-30 21:45 | C. MICKELSON | (858) 654-4130 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-10-30 17:35 | 2003-10-30 18:00 | 1 | 25 | 0 | 25 | 1730 CASTELLANA RD. | San Diego | 92137 | SD | 8"VC | 1 | 06/11/2003 | ROOTS | ROOTS GROWING IN CITY SEWER MAIN. | RODDED MAIN WITH FULL SIZE BLADE TO RELIEVE BLOCKAGE AND CLEAN MAIN. WILL TELEVISE MAIN. | N | N | N | None | None | DRIED UP AT EDGE OF ROAD 50 WEST OF OVERFLOWING MH. | N | Y | N
|  | City of San Diego | City of San Diego | 2003-11-04 21:45 | 2003-11-04 23:10 | 2 | 0 | LINE BREAK | 381088 | Fax (858) 571-6972 (RWQCB) | 2003-11-04 23:30 | MATT HAUER | (858) 654-4130 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-04 21:45 | 2003-11-04 23:10 | 0.5 | 2 | 0 | 2 | S. 49 ST CROSS OF SOLOLA AV | San Diego | 92113 | SD | 8" VC MAIN | 0 |  | LINE BREAK | UNKNOWN BLOCKAGE ON 8" VC MAIN | BLOCKAGE RELIEVED ITSELF. UNKNOWN CAUSE. FLUSHED STOPPAGE SECTION AND TWO UP AND DOWN, ALL 10-34. | N | N | N | None | None | DRIED UP IN STREET | N | Y | N |  |  | UNKNOWN BLOCKAGE ON 8"VC MAIN. BLOCKAGE RELIEVED ITSELF BEFORE ARRIVAL. TWO SECTIONS UP AND DOWN WERE CLEANED, ALONG WITH STOPPAGE SECTION. ALL MAINS ARE CLEAR.
|  | City of San Diego | City of San Diego | 2003-11-06 15:09 | 2003-11-06 15:30 | 1050 | 0 | OTHER | 381340 | Fax (858) 571-6972 (RWQCB) | 2003-11-10 12:30 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-06 15:09 | 2003-11-06 15:30 | 50 | 1050 | 0 | 1050 | 8795 Biological Grade | San Diego | 92093 | SD | 8" main | 0 |  | OTHER | pump trucks decanting in 8" main overloaded system causing spill | had trucks decant in larger main. | N | Y | Y | Pacific Ocean | None |  | N | Y | Y | Bay/Lagoon/Beach | 3 | Pump trucks decanting from force main break at pump sta. 29 overloaded 8" main. Per the Enviormental Health Dept - signs were picked up on 11-09-03.
|  | City of San Diego | City of San Diego | 2003-11-06 10:50 | 2003-11-06 12:40 | 260 | 245 | ROOTS | 381294 | Fax (858) 571-6972 (RWQCB) | 2003-11-06 19:20 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-06 10:50 | 2003-11-06 12:40 | 2 | 260 | 245 | 15 | 3495 Wisteria. Dr | San Diego | 92104 | SD | Main | 0 |  | ROOTS | System failure roots and paper towels were found in the main. | Rodded main to relieve blockage and flushed the main for city protection. | N | Y | N | None | None | The spill dissapated in the storm drain. | Y | Y | N |  |  | This job was referred to be televised .
|  | City of San Diego | City of San Diego | 2003-11-06 09:54 | 2003-11-07 18:54 | 75600 | 0 | FLOOD DAMAGE | 381288 | Fax (858) 571-6972 (RWQCB) | 2003-11-13 15:00 | kevin gensler | (858) 614-4014 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-06 09:54 | 2003-11-07 18:54 | 100 | 75600 | 0 | 75600 | 11480 North Torrey Rd | San Diego | 92093 | SD | 14" Ci Force Main | 0 |  | FLOOD DAMAGE | 14 CI Force main break | Contained spill and repair pipe. | N | n | y | Pacific Ocean | None |  | y | Y | y |  | 3 | Per. County Health signs picked up on 11/9/2003 after clean water sample results. Report finalized after spill volume calculations were completed.This was not a continuous spill. 48,040 Gals. On 11/6/03 & 27,560 on 11/7/03
|  | City of San Diego | City of San Diego | 2003-11-07 08:27 | 2003-11-07 10:07 | 280 | 265 | ROOTS | 381456 | Fax (858) 571-6972 (RWQCB) | 2003-11-07 15:15 | Melody Shaw-Sydnor |  | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-07 08:27 | 2003-11-07 10:07 | 2 | 280 | 265 | 15 | 3495 Wisteria. Dr | San Diego | 92104 | SD | Main | 0 |  | ROOTS | Roots found in main and pipe needs to be renewed. Area supvisor has been advised | Had TV crew televise main to locate exact location of roots in the main .Rodded the main and relieved the blockage . | N | Y | N | None | None | Dissapacted in the storm drain. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-11-21 14:42 | 2003-11-21 15:45 | 31.5 | 0 | ROOTS | 383291 | Fax (858) 571-6972 (RWQCB) | 2003-11-21 17:20 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-21 14:42 | 2003-11-21 15:45 | 0.5 | 31.5 | 0 | 31.5 | 1280 Brookes Tr | San Diego | 92103 | SD | 8" VC Main | 1 | 11/24/2002 | ROOTS | Blockage was caused by roots. | Rodder clear stop, also rodder cleaned two section up, unable to rod two down due a "T" conection on the canyon main. Refer to area supervisor for evaluation. | N | N | N | None | None | Dissipated in the side of the hill. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-11-22 12:32 | 2003-11-22 13:25 | 26.5 | 0 | ROOTS | 383429 | Fax (858) 571-6972 (RWQCB) | 2003-11-22 16:55 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-22 12:32 | 2003-11-22 13:25 | 0.5 | 26.5 | 0 | 26.5 | 1555 Gregory st | San Diego | 92102 | SD | 6"cp main | 1 | 06/27/2003 | ROOTS | Blockage was caused by roots. | Rodder clear stop, also rodded two sections up. Unable to rod two down due to no access (canyon). Refer to area supervisor for evaluation. | N | N | N | None | None | Dissipated in the side of the hill. | N | Y | N
|  | City of San Diego | City of San Diego | 2003-11-22 21:34 | 2003-11-22 21:45 | 5.5 | 0 | CONSTRUCTION | 383447 | Fax (858) 571-6972 (RWQCB) | 2203-11-23 14:00 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-22 21:34 | 2003-11-22 21:45 | 0.5 | 5.5 | 0 | 5.5 | 2200 Pacific Hwy | San Diego | 92101 | SD | 4" vc main | 0 |  | CONSTRUCTION | Reported as a BSO, unit found a 733. Debris blocking a 4" main. | Flushed main, vaccumed mh76. On 11/23/2003 rodder unit han-rod 4" main. Mh76 (fsn24618) is a wet/mh. In addition investigated that fsn24365, 8"cp main doesn't have flow to mh351 (fsn91741). Refer to area supervisor for evaluation. | N | N | N | None | None | Dissipated around of the mh. | N | Y | N
|  | City of San Diego | City of San Diego | 2003-11-23 15:38 | 2003-11-23 16:05 | 135 | 0 | FLOOD DAMAGE | 383475 | Fax (858) 571-6972 (RWQCB) | 2003-12-01 08:30 | Melody Shaw -for Carlos Gomez | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-23 15:38 | 2003-11-23 16:05 | 5 | 135 | 0 | 135 | 1747 Pacific Hwy | San Diego | 92101 | SD | 8" vc main | 0 |  | FLOOD DAMAGE | Blockage was caused by debris (rocks) | Rooder clear stop. In addition vactor contained spill. Unable to clean more than 25' from mh67, possible main collapse due to a previous repair of water conection. Refer to TV and area supervisor for further investigation. | N | Y | Y | San Diego Bay | NONE |  | Y | Y | N |  |  | Due at no public access no posting requiered per San Diego CDEH. City Construction crew made repairs on 11-29-03.
|  | City of San Diego | City of San Diego | 2003-11-23 14:57 | 2003-11-23 15:53 | 56 | 35 | GREASE | 383474 | Fax (858) 571-6972 (RWQCB) | 2003-11-23 19:40 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-23 14:57 | 2003-11-23 15:53 | 1 | 56 | 35 | 21 | 8th av & Washington | San Diego | 92103 | SD | 6" vc main | 0 |  | GREASE | 6"vc main grease blockages. | Flushed line to relieve stop. Call started as a 732, unit reported as a 733 upon arrival. Refer to area supervisor for evaluation. | N | Y | N | None | None | Dissipated in stormdrain system. | N | Y | N
|  | City of San Diego | City of San Diego | 2003-11-23 18:17 | 2003-11-23 21:15 | 356 | 356 | ROOTS | 383480 | Fax (858) 571-6972 (RWQCB) | 2003-11-24 10:00 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-23 18:17 | 2003-11-23 21:15 | 2 | 356 | 356 | 0 | 3705 10th ave | San Diego | 92103 | SD | 6" vc main | 0 |  | ROOTS | Blockage was caused by roots. | Reason of no "Overflow volume released to environment." Because sewage went back to the system into downstream mh514. Stop was cleared by han-rods. Refer to area supervisor for further investigation. | N | N | N | None | None | Went back to the system (mh514) | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-11-26 18:46 | 2003-11-26 22:00 | 388 | 330 | GREASE | 384151 | Fax (858) 571-6972 (RWQCB) | 2003-11-27 01:50 | C. MICKELSON | (858) 654-4130 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-26 18:46 | 2003-11-26 22:00 | 2 | 388 | 330 | 58 | MASON ST. X JUAN ST. | San Diego | 92110 | SD | 6" CP | 1 | 03/26/2003 | GREASE | GREASE BLOCKAGE IN SEWER MAIN. | VACTORED OVERFLOW. RODDED TO RELIEVE GREASE BLOCKAGE AND CLEAN PIPE. WASHED DOWN, VACTORED AND DEODORIZED AREA. WILL TELEVISE MAIN. | N | Y | N | None | None | DRIED IN STORM PIPE NEAR WALLACE ST. X CONGRESS ST. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-11-26 18:22 | 2003-11-26 18:50 | 28 | 0 | FLOOD DAMAGE | 384148 | Fax (858) 571-6972 (RWQCB) | 2003-11-27 01:30 | C. MICKELSON | (858) 654-4130 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-26 18:22 | 2003-11-26 18:50 | 1 | 28 | 0 | 28 | 1747 PACIFIC HIGHWAY | San Diego | 92101 | SD | 8" VC | 1 | 11/23/2003 | FLOOD DAMAGE | WATER SERVICE INSTALLED OVER SEWER MAIN CAUSING MAIN TO COLLASPE. | MACHINE RODDED AND HAND RODDED TO RESTORE FLOW. WILL MONITOR, TELEVISE, AND MAKE SPOT REPAIR. | N | Y | N | None | None | DRIED IN STORM PIPE IN FRONT OF 1747 PAC HWY. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-11-26 09:07 | 2003-11-26 10:20 | 2263 | 0 | ROOTS | 384088 | Fax (858) 571-6972 (RWQCB) | 2003-11-26 15:00 | Paul Anderson(OCA) | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-11-26 09:07 | 2003-11-26 10:20 | 31 | 2263 | 0 | 2263 | Fairmount Ave. & Montezuma Rd. | San Diego | 92115 | SD | 8" vc main | 0 | 0 | ROOTS | Flushed 8" sewer main to relieved stop of roots and rocks. Possible break in line. | Cleaned line until 10-34, and will refer to area supervisor and T.V. crews. | N | y | y | San Diego River | None |  | y | Y | N |  | 0 | Flush sewer main to relive line of roots and rocks , will refer to area supervisor and T.V.
|  | City of San Diego | City of San Diego | 2003-12-04 10:36 | 2003-12-04 12:58 | 700 | 600 | ROOTS | 385206 | Fax (858) 571-6972 (RWQCB) | 2003-12-04 18:45 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-12-04 10:36 | 2003-12-04 12:58 | 5 | 700 | 600 | 100 | 7014 Tuther.Way | San Diego | 92139 | SD | 8" VC Main | 0 |  | ROOTS | Blockage in the city main. (Roots) | Machine and hand rodded the main to relieve root blockage, and vactored and flushed the line for city protection. The main was televised on 12-04-03.City mains clear at departure. | N | Y | N | None | None | Dissapated in the storm drain | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-12-09 16:00 | 2003-12-09 18:40 | 480 | 405 | GREASE | 386346 | Fax (858) 571-6972 (RWQCB) | 2003-12-09 22:00 | C. MICKELSON | (858) 654-4130 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-12-09 16:00 | 2003-12-09 18:40 | 3 | 480 | 405 | 75 | CAMINO DEL RIO SO. X FAIRMONT AVE. | San Diego | 92115 | SD | 10' VC | 0 |  | GREASE | HEAVY GREASE BLOCKAGE IN CITY SEWER MAIN. | VACTORED OVERFLOW. FLUSHED MAIN TO RELIEVE GREASE BLOCKAGE. CLEANED 2 SECTIONS UPSTREAM AND 2 SECTIONS DOWNSTREAM. REFER TO HAVE MAIN TELEVISED. ADJUST CLEANING MAINTENANCE SCHEDULE. | N | Y | N | None | None | DISSIPATED IN STORM SYSTEM AT FAIRMONT SO. OF HWY 8. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-12-14 11:25 | 2003-12-14 11:50 | 12.5 | 0 | ROOTS | 387243 | Fax (858) 571-6972 (RWQCB) | 2003-12-14 15:25 | D.A. BRANCO | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-12-14 11:25 | 2003-12-14 11:50 | 0.5 | 12.5 | 0 | 12.5 | AMPUDIA ST & WHITMAN ST | San Diego | 92103 | SD | 6"cp | 2 | 4/4/2003 6-20-2003 | ROOTS | BLOCKAGE CAUSED BY ROOTS. | MACHINE ROD LINE TO RELIEVE STOP; CLEAN AREA; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-12-15 16:17 | 2003-12-15 17:20 | 630 | 20 | GREASE | 387398 | Fax (858) 571-6972 (RWQCB) | 2003-12-15 20:20 | C. MICKELSON | (858) 654-4130 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-12-15 16:17 | 2003-12-15 17:20 | 10 | 630 | 20 | 610 | 3728 MENLO AVE. | San Diego | 92105 | SD | 8" UNK | 1 | 07/08/2003 | GREASE | HEAVY GREASE IN CITY SEWER MAIN. | GREASE BLOCKAGE RELIEVED ITSELF AT TIME OF ARRIVAL. FLUSHED MAINS TO CLEAN. SWEPT, VACTORED AND DEODORIZED STREET. WILL REFER MAIN TO BE TELEVISED. | N | Y | N | None | None | DISIPPATED IN STORM SYSTEM AT EUCLID AVE. X HOME AVE. | Y | Y | N |  |  | MAIN OVERFLOWED FROM PROP. C/O AND BATHROOM AT 3728 MENLO AVE. (LOWER ELE. THAN MAIN MH).
|  | City of San Diego | City of San Diego | 2003-12-21 10:47 | 2003-12-21 11:45 | 1160 | 1160 | GREASE | 388328 | Fax (858) 571-6972 (RWQCB) | 2003-12-21 16:00 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-12-21 10:47 | 2003-12-21 11:45 | 20 | 1160 | 1160 | 0 | 4130 Altadena Av | San Diego | 92105 | SD | 10" PVC main | 1 | 07/08/2003 | GREASE | Blockage was caused by grease. | Rodder line to relieve stop, recovered sewer spill by vacuumed from strom drain channel. | N | Y | N | None | None | recovered from stormdrain channel | Y | Y | N
|  | City of San Diego | City of San Diego | 2003-12-22 17:56 | 2003-12-22 20:30 | 462 | 100 | GREASE | 388465 | Fax (858) 571-6972 (RWQCB) | 2003-12-22 22:15 | C. MICKELSON | (858) 654-4130 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-12-22 17:56 | 2003-12-22 20:30 | 3 | 462 | 100 | 362 | 4328 41ST ST. | San Diego | 92105 | SD | 6" VC | 1 | 04/20/2003 | GREASE | GREASE IN CITY SEWER MAIN. | FLUSH TO RELIEVE OVERFLOW AND CLEAN SEWER MAIN. REFER TO HAVE CITY MAIN TELEVISED. | N | Y | N | None | None | DRIED IN STORM BOX AT NW CORNER 41ST ST. X EL CAJON BL. | Y | Y | N |  |  | OVERFLOW CAME OUT OF PROPERTY C/Os AT 4328 AND 4334 41ST ST., FLOWING ONTO OUTSIDE PROPERTY AND SPILLING ONTO DIRT ALLEY AND STREET. C/O ELEVATIONS ARE LOWER THAN CITY MANHOLES.
|  | City of San Diego | City of San Diego | 2003-12-24 16:00 | 2003-12-26 07:30 | 59.4 | 0 | OTHER | 388825 | Fax (858) 571-6972 (RWQCB) | 2003-12-26 09:30 | Alice Benson | (619) 428-7320 | O&M | O&M | 2003-12-24 16:00 | 2003-12-26 07:30 | 0.12 | 59.4 | 0 | 59.4 | 2411 Dairy Mart. Rd | San Diego | 92154 | SD | PLT/STR-DRAIN | 0 |  | OTHER | Temp-pump was installed on 12-24-03 . The flapper valve was leaking and caused a small discharge. | Removed tempory pump on 12-26-03 | N | Y | Y | None | None | Dry channel area on South side of Tijuana River | Y | Y | N |  |  | Content of sanitary sewer is potable water primary from the pump seal: Sm-Volume from ordor control Valve.No staff on site using sanitary system.
|  | City of San Diego | City of San Diego | 2003-12-26 16:21 | 2003-12-26 16:55 | 17 | 0 | ROOTS | 388831 | Fax (858) 571-6972 (RWQCB) | 2003-12-26 20:05 | D.A. BRANCO | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2003-12-26 16:21 | 2003-12-26 16:55 | 0.5 | 17 | 0 | 17 | 1479 SAVOY CR | San Diego | 92107 | SD | 6"VC | 0 | 0 | ROOTS | BLOCKAGE CAUSED BY ROOTS. | MACHINE ROD TO RELIEVE STOP. REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | N | N | None | None | DRIED IN STREET. | N | Y | N
|  | City of Escondido | City of Escondido | 2003-08-30 08:00 | 2003-09-03 10:00 | 1470 | 200 | PRIVATE PROPERTY | 034001 | Fax - Bryan Ott 858-571-6972 | 2003-09-04 09:00 | John Vaught | (760)839-4323 | City of Escondido | City of Escondido | 2003-08-30 08:00 | 2003-09-03 10:00 | 0.25 | 1470 | 200 | 1270 | 2732 Old Spanish Trail | Escondido | 92025 | SD | Private septic field | 0 |  | PRIVATE PROPERTY | Mulfunctioning septic field | A Notice of Correction was issued to the property owner for unlawful discharge of seweage. | Y | Y | Y | Dead Horse Creek | None | Creek flows to dry lake (east end of Lake Hodges) then to soil. | Y | Y | Y | Public access points / Permanently posted through Kit Carson Park |  |  |  | x
|  | City of Escondido | City of Escondido | 10/10/2003 1230 | 10/10/2003 1250 | 120 | 20 | DEBRIS | 034002 | Fax - Brain Ott | 10/10/2003 1430 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 10/10/2003 1230 | 10/10/2003 1250 | 6 | 120 | 20 | 100 | 1815 N. Broadway | Escondido | 92025 | SD | Sewer manhole 712 | 0 |  | DEBRIS | The sewer main has a low point or belly which collects debris and caused the stoppage. | This sewer main is now on a six month cleaning schedule. | N | Y | Y | Reidy Creek | Escondido Creek | San Elijo Lagoon | Y | N | N | N/A
|  | City of Escondido | City of Escondido | 11/1/2003 700 | 11/1/2003 1230 | 660 | 200 | PRIVATE PROPERTY | 034003 | Fax - Brian Ott | 11/3/2003 1130 | Jim Miller | (760) 839-4323 | City of Escondido | City of Escondido | 11/1/2003 700 | 11/1/2003 1230 | 2 | 660 | 200 | 460 | 204 E. 2nd Ave. | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Private plumber failed to perform the proper maintenance to ensure reliability. | City Pretreatment inspector investigated the incident and issued the manager a Notice of correction for unlawful discharge of sewage. | Y | Y | Y | Escondido Creek | San Elijo Lagoon | San Elijo Lagoon | Y | N | N | N/A |  |  |  | x
|  | City of Escondido | City of Escondido | 11/25/2003 1650 | 11/25/2003 1700 | 50 | 50 | PRIVATE PROPERTY | 034004 | Fax - Brian Ott | 11/26/2003 1230 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 11/25/2003 1650 | 11/25/2003 1700 | 5 | 50 | 50 | 0 | 201 W. Grand Ave. | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private system | Customer was issued a lateral policy making then aware of their responsibilities for proper maintenance. | N | N | N |  |  |  | Y | N | N | N/A |  |  |  | x
|  | City of Escondido | City of Escondido | 12/02/2003 1058 | 12/02/3002 1115 | 17 | 17 | PRIVATE PROPERTY | 034005 | Fax - Brian Ott | 12/02/2003 1320 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 12/02/2003 1058 | 12/02/3002 1115 | 1 | 17 | 17 | 0 | 613 W. Valley Parkway | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private system | City sewer crew assisted private plumber in inspecting service lateral for structural problems, none was found. | N | Y | N |  |  |  | Y | N | N | N/A |  |  |  | x
|  | City of Escondido | City of Escondido | 12/11/2003 1130 | 12/11/2003 1200 | 30 | 15 | PRIVATE PROPERTY | 034006 | Fax - Brian Ott | 12/11/2003 1600 | Mike Schultz | (760) 839-4255 | City of Escondido | City of Escondido | 12/11/2003 1130 | 12/11/2003 1200 | 1 | 30 | 15 | 15 | 636 Fondale Ct. | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private system | The City will assist this customer in cleaning their service lateral every six months from the property line to the City main. | Y | Y | Y | Escondido Creek | San Elijo Lagoon | San Elijo Lagoon | Y | N | N | N/A |  |  |  | x
|  | City of Escondido | City of Escondido | 12/29/2003 2100 | 12/29/2003 2115 | 100 | 0 | DEBRIS | 034007 | Fax - Brian Ott | 12/30/2003 1100 | Jim Larzalere | (760) 839-4208 | City of Escondido | City of Escondido | 12/29/2003 2100 | 12/29/2003 2115 |  | 100 | 0 | 100 | 1521 S. Hale Ave. | Escondido | 92029 | SD | Wastewater Plant Building B | 0 |  | DEBRIS | Grit system malfunctioned causing cyclone seperator vent tube to discharge raw sewage into plant drainage system which flows to the storm system. | Clean & clear debris from cyclone seperator and verify proper operation of grit system. | Y | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A |  |  |  |  | p
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 07/23/03 - 12:05 | 07/23/03 - 13:05 | 300 | 6000 | Grease | 030401 | Clay Clifton | 07/23/03 - 15:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 07/23/03 - 12:05 | 07/23/03 - 13:05 | 5 | 300 | 6000 | 0 | 5980 Aenida Encinas | Carlsbad | 92008 | SD | Property line cleanout | 0 | N/A | Grease | Grease in lateral, coming from Marie Calendars | 1) Clean lateral regularly-add to priority cleaning list 2) We will evaluate condition | N | Y | Y | Drainage ditch | Cannon Lake | We recaptured in Creek after we flushed the gutter and strom drain system | Y | N | N | N/A | 0 | None |  | x
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 07/26/03 - 7:00 pm | 07/26/03 - 11:50 | 25 | 25 | Grease | 030402 | Clay Clifton | 04/21/03 - 10:45 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 07/26/03 - 7:00 pm | 07/26/03 - 11:50 | 0 | 25 | 25 | 0 | 2250 Avenida Magnifica | Carlsbad | 92008 | SD | Private sewer lateral | 1 | 2002-10-01 | Grease | 6" lateral backed up private spill. Plumber cleared stoppage 7/26/03, 11:50 pm | Plumber cleared stoppage | N | N | N | None | None | Recaptured by vactor | N | N | N | N/A | 0 | None |  | x
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 08/02/03 - 1:49 pm | 08/02/03 - 6:30 pm | 0 | 30 | Unknown | 030403 | Clay Clifton | 08/04/03 - 8:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 08/02/03 - 1:49 pm | 08/02/03 - 6:30 pm | 0 | 0 | 30 | 0 | 2250 Avenida Magnifica | Carlsbad | 92008 | SD | Private sewer lateral | 2 | 10/1/02, 7/26/03 | Unknown | Unknown | Plumber cleared lateral. HOA needs to do preventative maintenance. | N | N | N | None | None | Returned to lateral | Y | N | N | N/A | 0 | Property Manager Ann rios 760-434-6101 |  | x
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2003-08-02 12:59 | 08/02/03 - 1:00 pm | 300 | 600 | Pump Station Failure | 030404 | Clay Clifton | 08/04/03 - 8:30 am | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2003-08-02 12:59 | 08/02/03 - 1:00 pm | 300 | 300 | 600 | 0 | Carlsabd Blvd/Island | Carlsbad | 92008 | SD | Private lift station | 0 | N/A | Pump Station Failure | State Beach Lift Station failed | State Parks needs to do work on regular basis to prevent failures. *Supervisor said the alarm was vandalized. | N |  |  | Gutter along Carlsbad Blvd | Pacific Ocean | We recaptured the entire overflow and wash down clean-up water. | Y | N | N |  | 0 | We assisted the State Parks with containment and clean-up. |  | x
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 08/28/03 - 11:45 | 08/28/03 - 11:45 | 30 | 60 | Private Property | 030405 | Clay Clifton | 08/28/03 - 15:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 08/28/03 - 11:45 | 08/28/03 - 11:45 | 30 | 30 | 60 | 20 | 2665 Kremeyer Cr | Carlsbad | 92008 | SD | Private cleanout under garage | 1 | 2002-11-27 | Private Property | Sewer overflowing inside the Apartment complex. Maintenance worker removed the cleanout cap. Overflowing into the alley parking lot | We recommend for next time to contain sewer spill and we recommend more maintenance in the sewer laterals by their plumber | N | Y | N | None | None | Manhole | Y | N | N | N/A | 0 | Private overflow |  | x
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/18/03 - 18:00 | 10/18/03 - 18:45 | 45 | 0 | Construction | 030406 | Clay Clifton | 10/23/03 - 10:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/18/03 - 18:00 | 10/18/03 - 18:45 | 1 | 45 | 0 | 85 | Beachwood Ct | Carlsbad | 92008 | SD | Sewer Manhole | 0 | N/A | Construction | Contractor left trap in manhole. Caused system to back up | Insure that contractor does everything to make sure that there are no blockages. | N | Y | N | Storm drain inlet on Beachwood | None | Greenbelt-we rinsed the street, coned off area. Did not reach lagoon. | Y | N | N | N/A | 0 | None
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/30/03 - 7:30 | 10/30/03 - 7:55 | 75 | 75 | Roots | 060407 | Clay Clifton | 10/30/03 - 7:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/30/03 - 7:30 | 10/30/03 - 7:55 | 3 | 75 | 75 | 0 | 393 Oak | Carlsbad | 92008 | SD | Property line cleanout | 0 | N/A | Roots | Roots | Sewer rod more often | N | N | N | None | None | Dirt road | Y | N | N | N/A | 0 | None
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 11/23/03 - 10:45 | 11/23/03 - 11:30 | 60 | 60 | Roots | 030408 | Clay Clifton | 11/24/03 - 4:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 11/23/03 - 10:45 | 11/23/03 - 11:30 | 2 | 60 | 60 | 0 | 3175 Harding st | Carlsbad | 92008 | SD | Cleanout | 0 | N/A | Roots | Roots in 6" cleanout/Main | Water was shut off. Sewer was contained and cleaned up before entering storm drain. Lateralal was rodded and cleared, customer back in service, mainalso cleaned and flowing properly. | N | N | N | None | None | Contained before entering storm drain | Y | N | N | N/A | 0 | None
|  | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 12/11/03 - 15:30 | 12/11/03 - 15:31 | 0.5 | 0.5 | Roots | 030409 | Clay Clifton | 12/11/03 - 16:45 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 12/11/03 - 15:30 | 12/11/03 - 15:31 | 0.5 | 0.5 | 0.5 | 0 | 391 Redwood | Carlsbad | 92008 | SD | Toilet inside residence | 0 | N/A | Roots | Roots in main caused sewer main backup | Televise, schedule possible repair and/or corrective measures | Y | N | N | None | None | Bathroom floor, cleaned up by City staff. Pictures taken. | Y | N | N | N/A | 0 | None |  | x
|  | Ramona Municipal Water District | PRIVATE PROPERTY | 2003-10-15 | 2003-10-15 09:15 | 250 | 0 | BLOCKAGE | 034001 | N/A | 2003-10-15 10:00 | Earl Colia | 760-789-1330 | Ramona Municipal Water District | Ramona Municipal Water District | UNKNOWN | 2003-10-15 09:15 | 7 | 250 | 0 | 250 | 1029 H st | Ramona | 92065 | SD | private sewer lateral under home | 0 | N/A | BLOCKAGE | household trash bloked sewer line, tenant removed cap | snaked clear amd replaced cap | N | N | N | none | none | backyards of 634 and 640 11th st. Ramona, Ca | Y | N | N | N/A | 0 | PRIVATE spil, NOT RMWD liability. Majority of spill in yard of 640 11th st. |  | x
|  | City of Solana Beach | City of Solana Beach | 2003-10-15 14:45 | 2003-10-15 15:00 | 7.5 | 4 | BLOCKAGE | 020302 | Yes 858 636-3155 | 2003-10-16 09:00 | Danny King | 858 720-2477 | City of Solana Beach | City of Solana Beach | 2003-10-15 14:45 | 2003-10-15 15:00 | 0.5 | 7.5 | 4 | 3.5 | 143 S. Cedros | Solana Beach | 92075 | SD | Sewer Cleanout | 0 | N/A | BLOCKAGE | Backup | Dam was installed at catch basin and vac truck called | N | Y | N | Not reached went to low flow diverter only | Pacific Ocean |  | Y | N | N |  |  | See spill incident report for more information
|  | City of Solana Beach | City of Solana Beach | 2003-10-09 14:00 | 2003-10-09 16:10 | 260 | 100 | BLOCKAGE | 020303 | No - just DEH | 2003-10-16 09:00 | Danny King | 858 720-2477 | City of Solana Beach | City of Solana Beach | 2003-10-09 14:00 | 2003-10-09 16:10 | 20 | 260 | 100 | 160 | 530 Lomas Santa Fe | Solana Beach | 92075 | SD | Sewer Cleanout | 1 | 530 Lomas Santa Fe | BLOCKAGE | Backup | Pipe was cleared - vac truck was called to cleanup excess | N | Y | N | Stevens Creek dry | San Dieguito Lagoon |  | Y | N | N |  |  | See spill incident report for more information
|  | City of Solana Beach | City of Solana Beach | 2003-10-17 09:45 | 2003-10-17 09:50 | 500 | 450 | CONSTRUCTION | 020304 | yes 858 636-3155 | 2003-10-21 16:50 | Danny King | 858 720-2477 | City of Solana Beach | City of Solana Beach | 2003-10-17 09:45 | 2003-10-17 09:50 | 100 | 500 | 450 | 50 | 440 Stevens | Solana Beach | 92075 | SD | Manhole | 0 | N/A | CONSTRUCTION | Construction Mistake - capped manhole without redirecting flow | most sewage backed up in businesses - small amt. reached storm drain - contained in channel | N | Y | N | Stevens Creek dry | San Dieguito Lagoon |  | Y | N | Y | caution tape around outfall |  | See spill incident report for more information
|  | City of Solana Beach | City of Solana Beach | 2003-11-04 11:30 | 2003-11-04 12:30 | 30 | 10 | BLOCKAGE | 020305 | No - just DEH | 2003-11-04 16:30 | Danny King | 858 720-2477 | City of Solana Beach | City of Solana Beach | 2003-11-04 11:30 | 2003-11-04 12:30 | 0.5 | 30 | 10 | 20 | 514 Via de la Valle | Solana Beach | 92075 | SD | Sewer Cleanout | 0 | N/A | BLOCKAGE | Appeared to be grease in pipe | Contained flow until vac truck arrived | N | Y | N | Stevens Creek | San Dieguito Lagoon |  | Y | N | N |  |  | See spill incident report for more information
|  | City of National City | City of National City | 2003-11-30 20:30 | 2003-12-01 07:30 | 3300 | 300 | UNKNOWN |  | FAX toDavid Hanson | 12/1/03 1030 hrs | Joe Smith | 619 336-4587 | National City |  | 11/30/03 20:30 hrs | 12/1/03 0730 |  | 3300 | 300 |  | 2000 BLK 7th @ T ave. | National City | 91950 | SD | 1749 | 0 |  | unknown | partial blockage in 6 inch main cause unknown | blockage removed all affected areas cleaned & sanitizes. Some water recoved and returned to sewer system |  | y | n | n/a | n/a | 20 inch storm drain | y | n | n |  |  | affected storm drain in a closed concrete system running under the most of the city for 2 miles before reaching san diego bay.
|  | City of National City | City of National City | 2003-12-22 13:00 | 2003-12-22 23:00 | 0 | 0 | DEBRIS |  | FAX toDavid Hanson | 12/22/03 0815 hrs | Joe Smith | 619 336-4587 | National City |  | 12/22/03 1300 hrs | 12/22/03 2300 hrs |  | Unknown | all |  | 1427 Sheryl Lane | National City | 91950 | SD | 227 | 0 |  | Debris | partial blockage in 6 inch main cause by debris from an unknown source | all debris removed from manhole no overflow to public area water. All affected areas cleaned & sanitizes. Some water in private home was removed and returned to sewer system by restoration company |  | n | n | n/a | n/a | Private home | y | n | n |  |  | confined to private home. Restoration company called to clean and sanitize basement of home.No water in street or storm drain.
|  | City of Poway | City of Poway | 2003-12-29 15:15 | 2003-12-29 15:35 | 200 | 0 | ROOTS | 034001 | Faxed | 2003-12-30 10:15 | Brad Voorhees | 858/679-5419 | City of Poway | City of Poway | 2003-12-29 15:15 | 2003-12-29 15:35 | 10 | 200 | 0 | 200 | 200 ft w/o 16711 Martincoit Rd | Poway | 92064 | SD | Concrete encasement | 0 |  | ROOTS | Partial blockage in 12-inch sewer main that runs along Green Valley Creek, approx 200 ft w/o 16711 Martincoit Rd. Roots are the probably cause; leakage was out of the pipe joints in concrete encasement. Spill not recovered due to it following the creek. | The blockage was cleared using the Vactor unit. A video inspection is scheduled in order to determine extend of damage to the pipe and the encasement, and to determine repair method(s). | Y | N | Y | Green Valley Creek | Green Valley Creek |  | Y | N | Y | Along Green Valley Creek, Martincoit Road and Calle Colina. | 5 | 2nd quarter 2003.
|  | City of Poway | City of Poway | 2003-12-31 09:00 | 2003-12-31 09:30 | 500 | 0 | LINE BREAK | 034002 | Faxed | 2003-12-31 12:00 | Brad Voorhees | 858/679-5419 | City of Poway | City of Poway | 2003-12-31 09:00 | 2003-12-31 09:30 | 17 | 500 | 0 | 500 | 200 ft w/o 16711 Martincoit Rd | Poway | 92064 | SD | Concrete encasement | 1 | 37985 | LINE BREAK | Partial blockage in 12-inch sewer main that runs along Green Valley Creek, approx 200 ft w/o 16711 Martincoit Rd (same location as 12/30/03). The blockage was cleared using the Vactor unit; a line break is the probable cause (in the concrete encasement). Spill unrecoverable due to flow directly into creek. | Crew cleaned the main with the Vactor. A video inspection was performed at midnight, 12/30/03, to determine extent of damage and repairs needed. Flow as normal at time of video inspection. | N | N | Y | Green Valley Creek | Green Valley Creek |  | Y | N | Y | Along Green Valley Creek, Martincoit Road and Calle Colina. | 5 | Contractor is setting up a BYPASS system. The line will be taken out of service and bypassed until repairs can be made. BYPASS should be installed by 5:00 p.m. 12/31/03; City crews are standing by until the BYPASS can be installed.
|  | Padre Dam Municipal Water District | Padre Dam Municipal Water District | 2003-10-07 06:15 | 2003-10-07 07:05 | 50000 | 25000 | OTHER | 034001 | David Hanson | 2003-10-07 | Martin Holmes | (619) 258-4706 | Padre Dam Municipal Water District | Padre Dam Municipal Water District | 2003-10-07 06:15 | 2003-10-07 07:05 | 1000 | 50000 | 25000 | 25000 | 9120 Carlton Oaks Drive | Santee | 92071 | SD | 8" pipe outside IPS | 0 | None | OTHER | 8" ductile iron pipe for surge tank, bolts at flange rusted or were eaten away over years, broke. Surge tank connected to influent pump station. | 8" pipe removed and blind flange put on with stainless steel bolts. Will uncover 2nd surge pipe and check for bad bolts and replace. | N | Y | Y | Sycamore Creek | Santee Lakes / Lakes 1 &2 | N/A | Y | Y | Y | Country Club Ponds & Lakes 1 & 2 | 7 | Signs are posted around at Carlton Oaks Country Club and Lakes 1 & 2 at Santee Lakes Park
|  | Vallecitos Water District | Vallecitos Water District | 2003-09-10 10:45 | 2003-09-10 12:09 | 200 | 200 | Construction | 034001 | David Hanson | 09/11/03 1355 | Rich Arrant | 760-744-0460 | Vallecitos Water District | Vallecitos Water District | 09/10/03 1045 | 09/10/03 1209 | 2.4 | 200 | 200 | 0 | Liberty Dr. | San Marcos | 92069 | SD | 8" sewer | 0 | N/A | Construction | Const.track hoe broke line | Line was repaired | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | 0 | None
|  | Vallecitos Water District | Vallecitos Water District | 2003-09-19 11:05 | 2003-09-19 11:10 | 70 | 70 | Construction | 034002 | David Hanson | 09/24/03 1018 | Rich Arrant | 760-744-0460 | Vallecitos Water District | Vallecitos Water District | 09/19/03 1105 | 09/19/03 1110 | 14 | 70 | 70 | 0 | RSF/Via Alondra | San Marcos | 92069 | SD | 8" sewer | 1 | N/A | Construction | Const. Blocked M/H | Blockage cleared | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | 0 | None
|  | Vallecitos Water District | Vallecitos Water District | 2003-11-14 07:35 | 2003-11-14 07:55 | 300 | 0 | DEBRIS | 034003 | David Hanson | 11/14/03 1320 | Corey Harrell | 760-744-0460 | Vallecitos Water District | Vallecitos Water District | 11/14/03 0735 | 11/14/03 0755 | 15 | 300 | 0 | 300 | Easement | San Marcos | 92069 | SD | 4" siphon | 0 | N/A | DEBRIS | Debris caused blockage | Blockage cleared | Y | N | N | N/A | N/A | Ground | Y | N | N | N/A | 0 | None
|  | Vallecitos Water District | Vallecitos Water District | 2003-11-21 08:30 | 2003-11-21 11:15 | 55 | 55 | ROOTS | 034004 | David Hanson | 11/21/03 1321 | Corey Harrell | 760-744-0460 | Vallecitos Water District | Vallecitos Water District | 11/21/03 0830 | 11/21/03 1115 | 5 | 55 | 55 | 0 | Via Camellia | San Marcos | 92069 | SD | 8" sewer | 0 | N/A | ROOTS | Root Blockage | Blockage cleared | N | N | N | N/A | N/A | Vactored up | Y | N | N | N/A | 0 | None
|  | City of Chula Vista | City of Chula Vista | 2003-08-30 10:00 | 2003-08-30 11:00 | 1000 | 800 | DEBRIS | 034463 | 1-858-565-5255 | 8/30/03 1:04pm | Mark Sanchez | 619-397-6025 | City of Chula Vista | City of Chula Vista | 8/30/03 10:00am | 2003-08-30 11:00 | 5 | 1000 | 800 | 200 | Brandywine ave | Chula Vista | 91911 | SD | Sewer M/H 7125 | 0 | 0 | DEBRIS | Grease & Rags | Flush broke plug followed line down stream line was rodded & filmed | N | Y | N | none | none | Storm drain catch basin | Y | Y | N | n/a | 0 | Spill enter catch basin but was contained and vacuumed
|  | City of Chula Vista | City of Chula Vista | 2003-07-13 11:35 | 2003-07-13 13:35 | 1800 | 1000 | GREASE | 033524 | 1-858-565-5255 | 7/13/03 3:pm | Mark Sanchez | 916-397-6025 | City of Chula Vista | City of Chula Vista | 7/13/03 11:35am | 2003-07-13 13:35 | 15 | 1800 | 1000 | 800 | 17 Oxford st | Chula Vista | 91911 | SD | Sewer M/H 5672 | 0 | 0 | GREASE | Large chunck of grease | Flushed main Rodded and filmed line | N | Y | N | none | none | Storm drain Anita/Fresno | Y | Y | Y | South side Main/Fresno | 3 | Storm drain was flushed and vacuumed
|  | City of Chula Vista | City of Chula Vista | 2003-11-08 21:00 | 2003-11-10 10:30 | 1985.5 | 0 | PRIVATE PROPERTY | 111003 | 1-858-571-6972 | 11/10/2003-1410 | CV Police Dept. | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 11/8/03-2100 | 11/10/03-10:30 | 0.9 | 1985.5 | 0 | 1985.5 | 288 Broadway | Chula Vista | 91910 | SD | Private Sewer cleanout from sewer main | 0 | N/A | PRIVATE PROPERTY | Private property main stoppage. Manager stated the problem started on 11/8/03 at 9:00 PM. Plumber cleared stoppage on 11/10/03 at 1030. Sewer spilled into the enviorment after a resident removed a cleanout cap, | Problem corrected by plumber, city crews wash and vaccumed up residue from spill | N | Y | Y | San Diego Bay | San Diego Bay | N/A | Y | N | N | N/A | N/A | Estimates are based on ten moble homes spilling 265 EDU's for 1.5 days |  | X
|  | City of Chula Vista | City of Chula Vista | 2003-11-23 19:00 | 2003-11-23 21:15 | 33.75 | 10 | PRIVATE PROPERTY | 112303 | 1-858-571-6972 | 11/23/03-2050 | CV Police Dept. | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 11/23/03-1900 | 11/23/03-21:15 | 0.25 | 33.75 | 10 | 23.75 | 363 Roosevelt | Chula Vista | 91910 | SD | Private sewer lateral cleanout | 0 | N/A | PRIVATE PROPERTY | Private sewer lateral stoppage | City contained spill until pumber cleared stoppage | N | Y | N | N/A | N/A | Stormdrain | Y | N | N | N/A | N/A | City provided containment, vaccumed and cleaned gutter line.Will assist homeowner in locating property line cleanout. |  | X
|  | City of Chula Vista | City of Chula Vista | 2003-12-01 09:15 | 2003-02-01 10:15 | 60 | 60 | GREASE | 121003 | 1-858-571-6972 | 12/1/03-0930 | CV Public Works | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 12/1/03-09:15 | 2/1/03-10:15 | 1 | 60 | 60 | 0 | 345 G Street | Chula Vista | 91910 | SD | Private sewer lateral cleanout | 0 | N/A | GREASE | Roots in city sewer main | City contained spill until sewer main stoppage was cleared. Rod sewer main & CCTV. | N | N | N | N/A | N/A | Curb | Y | N | N | N/A | N/A | City containment, vaccumed and cleaned gutter line. Line rodded and wil CCTV.
|  | City of Chula Vista | City of Chula Vista | 2003-12-01 08:15 | 2003-12-01 08:50 | 100 | 0 | ROOTS | 120103 | 1-858-571-6972 | 12/1/03-0830 | CV Public Works | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 12/1/03-08:15 | 12/1/03-08:50 | 5 | 100 | 0 | 100 | 1046 Second Ave. | Chula Vista | 91910 | SD | Manhole | 0 | N/A | ROOTS | Roots in city sewer main | Main cleaned with Hydro sewer flusher | N | N | N | N/A | N/A | Back yard of private resident | Y | N | N | N/A | N/A | Mh loc. In the back yard of private resident. Ground absorbed overflow. Area disinfected.
|  | City of Chula Vista | City of Chula Vista | 2003-12-24 10:00 | 2003-12-24 12:00 | 120 | 75 | BLOCKAGE | 122403 | 1-858-571-6972 | 12/24/03-10:00. | Apartment Mgr. | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 12/24/03-10:00 | 12/24/03-12:00 | 1 | 120 | 75 | 45 | 210 H Street | Chula Vista | 91910 | SD | Cleanout | 0 | N/A | BLOCKAGE | Private sewer lateral stoppage | Manager to expose cleanout to rod entire line | N | Y | N | N/A | N/A | Catch basin | Y | N | N | N/A | N/A |  |  | X
|  | City of Chula Vista | City of Chula Vista | 2003-12-24 10:15 | 2003-12-24 10:45 | 15 | 15 | BLOCKAGE | 122403 | 1-858-571-6972 | 12/24/03-10:30 | Wastewater Div. | (619) 397-6025 | City of Chula Vista | City of Chula Vista | 12/24/03-10:15 | 12/24/03-10:45 | 0.5 | 15 | 15 | 0 | 585 Palomar St. | Chula Vista | 91910 | SD | Cleanout | 0 | N/A | BLOCKAGE | Private sewer lateral stoppage. Cause was excess tolet paper | Lateral was cleared by city staff. Lateral to be scheduled for repair. | N | Y | N | N/A | N/A | Catch basin | Y | N | N | N/A | N/A | Lateral at Jack in the Box plugged. Line was rodded and sewer contained in a catch basin |  | X
|  | City of Del Mar | City of Del Mar | 2003-07-17 15:16 | 2003-07-17 15:32 | 32 | 0 | ROOTS | 034001 | Quarterly Report | N/A | David Zilberberg | (858) 755-3294 | City of Del Mar | City of Del Mar | 2003-07-17 15:16 | 2003-07-17 15:32 | 2 | 32 | 0 | 32 | Maiden Lane & Alley at manhole #46 | Del Mar | 92014 | SD | Manhole #46 Del Mar GIS map B-7 | 1 | 37779 | ROOTS | Roots | Rodded sewer main from 14th Street along Maiden Lane southbound to manhole #46 at the Alley over a total of 195 feet | N | N | N | none | none | Street surface of 14th Street, swept street clean | Y | N | N | N/A | 0 | The root cluster was most likely released from a private lateral when it was cleaned by a plumber MAINTENANCE OF LATERALS ARE RESIDENTS RESPONSIBILITY, PER CITY ORDINANCE No 472 (02/02/87), Chapter 22.08.070
|  | City of Del Mar | City of Del Mar | 2003-09-08 11:30 | 2003-09-08 11:31 | 1 | 0 | PRIVATE PROPERTY | 034002 | Quarterly Report | N/A | Kipling Curry | (858) 755-3294 | City of Del Mar | City of Del Mar | 2003-09-08 11:30 | 2003-09-08 11:31 | 1 | 1 | 0 | 1 | 315 El Amigo Rd. | Del Mar | 92014 | SD | Private lateral spill at 315 El Amigo Rd., Del Mar GIS map B10 | 0 | N/A | PRIVATE PROPERTY | Plugged Private Lateral | Called owner and advised of overflow, they called plumber to clear lateral. | N | N | N | none | none | Street surface at 315 El Amigo Rd., swept street clean | Y | N | N | N/A | 0 | Private residential sewer lateral overflow at 310 El Amigo Rd. City cleaned main and reported to resident. Lateral stoppage was cleared by resident's hired plumber. MAINTENANCE OF LATERALS ARE RESIDENTS RESPONSIBILITY, PER CITY ORDINANCE No 472 (02/02/87), Chapter 22.08.070 |  | X
|  | City of Imperial Beach | City of Imperial Beach | 2003-10-27 11:00 | 2003-10-27 11:20 | 45 | 45 | PRIVATE PROPERTY | 034001 | N/A | 10/25/03 1100 | B.Cordova | (619)628-1372 | City of Imperial Beach | City of Imperial Beach | 2003-10-27 11:00 | 2003-10-27 11:20 | 1 | 45 | 45 | 0 | 536 Florence Ave. | City of Imperial Beach | 91932 | SD | Lateral Cleanout | 0 | N/A | PRIVATE PROPERTY | Private lateral spill from private residence. | A plumber was called to correct the problem. The Vator truck came to vacuum up the spill. | N | N | N | none | none | Plumber Cleaned | N | N | N | N/A | 0 | This spill had a plumber on scene.This was a private lateral issue only. |  | X
|  | City of Imperial Beach | City of Imperial Beach | 2003-11-18 09:57 | 2003-11-18 10:25 | 158 | 158 | BLOCKAGE | 034002 | N/A | 11/18/03 0950 | Sheriff Department | (619)429-8311 | City of Imperial Beach | City of Imperial Beach | 11/18/03 0957 | 11/18/03 1025 | 5 | 158 | 158 | 0 | 221 Donax Ave. | City of Imperial Beach | 91932 | SD | M/H # 53 | 1 | 37754 | BLOCKAGE | Roots and grease found in the sewer main line. | Vactor truck jetted from M/H#52 to M/H#53 to alleviate blockage. Vactor then sent to Palm and Seacoast catch basin to recover. Gutters cleaned by fresh water wash-and broom down from Graffiti removal truck from spill site to Vactor. | N | Y | N | none | none | Sewer | N | N | N | N/A | 0 | Sewerage from this part of town will never reach surface waters. Storm drain wet-well will collect and then be pumped to the sewer
|  | City of Imperial Beach | City of Imperial Beach | 2003-12-10 | 2003-12-11 11:45 | 200 | 50 | PRIVATE PROPERTY | 034003 | fax# 858-5716972 | 2003-12-11 16:31 | AJ Moeller | (619) 628-1372 | City of Imperial Beach | City of Imperial Beach | 12/10/03 unknown | 12/11/03 1145 | 1 | 200 | 50 | 150 | 935 13th st. | City of Imperial Beach | 91932 | SD | Lateral clenout | 0 | N/A | PRIVATE PROPERTY | Private lateral spill from private residence. | A plumber was called to correct the problem. The Vator truck came to vacuum up the spill. | Y | Y | Y | POND 20 | none |  | Y | N | N | N/A | 0 | This was detected at 1030,we talk to the owner and they stopped using water by 1145,wecompleted the above ground cleanup process,the spill reached the storm drain,this is located in the citi of San Diego.We contacted Gary Dobbs,from S. D. sewer response team (619)980-3021 0 he stated that since they were traces of rain the policy oas not to clean the storm drainpipes.He refused to clean the storm drain. |  | X
|  | City of Imperial Beach | City of Imperial Beach | 2003-12-16 22:45 | 2003-12-16 23:50 | 65 | 65 | GREASE | 034004 | N/A | 12/16/03 2300 | CAL-AM | (619) 575 1106 | City of Imperial Beach | City of Imperial Beach | 12/16/03 2245 | 12/16/03 2350 | 1 | 65 | 65 | 0 | 7 St. and Baswood | City of Imperial Beach | 91932 | SD | M/H #197 | 1 | 37626 | GREASE | Roots and grease found in the sewer main line. | The duty person had alleviated the blockage and done the clean out.The4 catch basin was cleaned and the storm drain line cleaned to the distance of 90 feet. The following day , the line was fully cleaned from start of the line to the pump station. | N | Y | N | none | none | Sewer | Y | N | N | N/A | 0 | This spill was a direct result of agrease blockage in the sewer main.The Vactor crew was schedule to clean this entire section of town with in the next two weeks,This is a trouble line due top a belly on the main line between M/H#208 & M/H # 207
|  | City of Coronado | City of Coronado | 2003-09-01 11:00 | 2003-09-01 16:00 | 100 | 100 | GREASE | 034001 | Quarterly Report | N/A | N/A | N/A | City of Coronado | City of Coronado | 2003-09-01 11:00 | 2003-09-01 16:00 | 0.33 | 100 | 100 | 0 | Alameda/J alley at 10th Street | Coronado | 92118 | SD | Sewer Main | 0 | N/A | GREASE | Grease and rag in sewer main | Jetted out sewer line twice, vacuumed up spill, disinfected | N | N | N | None | None | Vacuumed up and removed | Y | N | N | N/A
|  | City of Coronado | City of Coronado | 2003-11-06 14:20 | 2003-11-06 15:30 | 5 | 5 | ROOTS | 034002 | Fax | 2003-11-06 16:00 | C. Kamenides | 619-522-7387 | City of Coronado | City of Coronado | 2003-11-06 14:20 | 2003-11-06 15:30 | 0.07 | 5 | 5 | 0 | 900 blk A/B alley | Coronado | 92118 | SD | Sewer main line | 0 |  | ROOTS | Main line blocked, possibly with roots | Rodded and jetted, applied foam, videotaped line | bar: N to N; Y to N
|  | Leucadia County Water District | Leucadia County Water District | 2003-07-23 07:23 | 2003-07-23 07:45 | 500 | 200 | DEBRIS |  | fax | 2003-09-08 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2003-07-23 07:23 | 2003-07-23 07:45 | 20 | 500 | 200 | 300 | 1100 Block Rancho Santa Fe Rd | Encinitas | 92024 | SD | Manhole # 08-0390 | 0 | NA | DEBRIS | 14" piece of composite gasket material blocked sewer | Cleaned line, inspeted line w/CCTV Inspection | N | Y | Y | Batiquitos Lagoon | Pacific Ocean | Pacific Ocean | Y | N | N | N/A | 0 | DEHS determined spill did not require posting.
|  | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-07-09 14:30 | 2003-07-09 14:40 | 50 | 0 | BLOCKAGE | 0304001 | David Hanson, fax (858) 467-2952 | 7/9/2003 14:30:00 PM | Rob Chichester | (619) 524-6417 | Navy Public Works | Navy Public Works | 2003-07-09 14:30 | 2003-07-09 14:40 | 5 | 50 | 0 | 0 | Subase South of Bldg. 215 | San Diego | 92136 | SD | Manhole | 0 | N/A | Blockage | Unknown blockage in swer line caused overflow. | Hydroblasted line clear. Overflow evaporated in parking lot. Area was cleaned and disinfected as per PWC Sewer Spill cleanup SOP. | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A | Requested a camera to check line for root intrusion to ensure future spills do not occur at site.
|  | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-07-20 13:45 | 2003-07-20 14:00 | 2500 | 1000 | PUMP STATION FAILURE | 0304002 | David Hanson, fax (858) 467-2952 | 2003-07-20 13:45 | Craig Smith | (619) 522-8680 | Navy Public Works | Navy Public Works | 2003-07-20 13:45 | 2003-07-20 14:00 | 167 | 2500 | 1000 | 1500 | Fidler Cove Marina | Coronado | 92135 | SD | Pump Station | 0 | N/A | Pump Station Failure | Pump station controller failed. Bubbler got plugged. | Clean and overhauled bubbler. | N | N | Y | San Diego Bay | San Diego Bay | San Diego Bay | Y | Y | Y | Along beach of Fiddlers Cove (military only area) | 4 | OES Control #03-3658. Site was cleaned per PWC sewer overflow cleanup SOP. Signs pulled on July 23, 2003.
|  | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-10-20 12:00 | 2003-10-20 13:00 | 150 | 120 | BLOCKAGE | 0304003 | David Hanson, fax (858) 467-2952 | 2003-10-20 11:15 | Rob Chichester | (619) 524-6417 | Navy Public Works | Navy Public Works | 2003-10-20 12:00 | 2003-10-20 13:00 | 2.5 | 150 | 120 | 30 | MCAS MIRAMAR Bldg. 9220, Boyington St. | San Diego | 92143 | SD | Manhole/ Catch Basin | 0 | N/A | Blockage | Contractor emptied a porta-potty during Miramar air show into the wrong location. | Cleaned out catch basin going into sewer. The un-recovered overflow evaporated on the lot. Area was cleaned and disinfected as per PWC Sewer Spill cleanup SOP. | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A | Cleared the blockage. Site was cleaned per PWC sewer overflow cleanup SOP.
|  | City of Lemon Grove | City of Lemon Grove | 2003-07-09 08:40 | 2003-07-09 17:30 | 300 | 225 | ROOTS | 034001 | this report | 2003-07-09 17:00 | D Catone | (619) 825-3810 | City of Lemon Grove | City of Lemon Grove | 2003-07-09 08:40 | 2003-07-09 17:30 | 5 | 300 | 225 | 75 | 2211 Massachusetts | Lemon Grove | 91945 | SD | 479-48-01 | 0 | 0 | roots | roots growing from private service connection | root cut main line | N | Y | N | none | none | storm drain empties into an open earthen browe ditch est 1000 ft long. Absorbed by earth | Y | N | N | none | 0 | main line was root cut. Check in 6 monthsfor possible connection repair
|  | City of Lemon Grove | City of Lemon Grove | 2003-10-04 11:00 | 2003-10-04 13:00 | 240 | 120 | UNKNOWN | 034002 | FAX | 2003-10-07 15:35 | D Catone | (619) 825-3810 | City of Lemon Grove | City of Lemon Grove | 2003-10-04 11:00 | 2003-10-04 13:00 | 2 | 240 | 120 | 120 | 7820 Lansing Dr | Lemon Grove | 91945 | SD | 577-18-05 | 0 | 0 | UNKNOWN | Stoppage relieved itself prior to jetting attempt | No debris found in lower MH after jetting. Segment cleaned & televissed 10/6/03 | N | N | N | none | none | Unimproved R-O-W. Absorbed into dirt & decomposed granite. | Y | N | Y | 7820 Lansing Dr | 3 | Line TV'd. No obstruction found.
|  | City of Lemon Grove | City of Lemon Grove | 2003-12-02 10:30 | 2003-12-02 12:05 | 475 | 325 | VANDALISM | 034003 | FAX | 2003-12-04 08:25 | D Catone | (619) 825-3810 | City of Lemon Grove | City of Lemon Grove | 2003-12-02 10:30 | 2003-12-02 12:05 | 5 | 475 | 325 | 150 | 3037 Crane St | Lemon Grove | 91945 | SD | 503-24-02 | 0 | 0 | VANDALISM | Rocks and debris removed from manhole | Line cleaned, televised. Manhole sealed with concrete | N | Y | N | none | none | diverted to dirt ditch.storm drain channel blocked w/sandbags. | N | N | N | none | 0 | Line is within nursery on dirt easement & was upgraded by Caltrans for new SR125 3 yrs ago
|  | Otay Water District | Otay Water District | 2003-11-27 11:10 | 2003-11-27 12:00 | 250 | 0 | BLOCKAGE | 034001 | N/A | 2003-11-28 15:30 | Dale Kreinbring | 619-670-2271 | Otay Water District | Otay Water District | 2003-11-27 11:10 | 2003-11-27 12:00 | 5 | 250 | 0 | 250 | Avocado W. 1N Campo D | La Mesa | 91941 | SD | MH C-3-1 | 0 | N/A | BLOCKAGE | A stainless steel bucket and baseball was found lodged inside the gravity main line downstream from the overflow manhole. | The bucket was removed and the entire line was T.V.'d and hydro-jetted back to the plant. | N | Y | N | None | None | The sewage flowed into the concrete stormdrain collection structure where it stopped and evaporated. | Y | N | N | N/A | 0
|  | City of La Mesa | City of La Mesa | 2003-07-25 14:55 | 2003-07-25 15:15 | 100 | 0 | UNKNOWN | 03-1 | N/A | 07/25/03 | David Schoolcraft | (619) 871-1613 | City of La Mesa | City of La Mesa | 07/25/03, 2:55 pm | 07/25/03, 3:15 pm | 5 | 100 | 0 | 100 | 4801 Jessie St. | La Mesa | 91941 | SD | 6 inch clay pipe | 0 | N/A | UNKNOWN | Unknown | Rodded line | N | Y | N | None | None | storm drain system | Y | N | N | N/A | 0
|  | City of La Mesa | City of La Mesa | 2003-08-14 15:15 | 2003-08-14 15:20 | 5 | 0 | OTHER | 03-2 | N/A | 08/14/03 | Steve Clark | (619) 667-1134 | City of La Mesa | City of La Mesa | 08/14/03, 3:15 pm | 08/14/03, 03:20 pm | 1 | 5 | 0 | 5 | 8125 Fletcher Parkway | La Mesa | 91941 | SD | private portapotty | 0 | N/A | OTHER | Portapotty in Costco parking lot overflowed | The portapotty company (PortoSan) was called out immediately to pump out tank, and Costco mgmt was educated on SSO issues. | N | Y | N | Alvarado Channel | SD River | storm drain system | Y | N | N | N/A | 0 |  |  | X
|  | City of La Mesa | City of La Mesa | 2003-09-10 07:00 | 2003-09-10 09:00 | 600 | 300 | CONSTRUCTION | 03-3 | N/A | 09/10/03 | Steve Clark | (619) 667-1134 | City of La Mesa | City of La Mesa | 09/10/03, 07:00 am | 09/10/03, 09:00 am | 5 | 600 | 300 | 300 | 7241 Alvarado Rd | La Mesa | 91941 | SD | 21 inch clay pipe | 0 | N/A | CONSTRUCTION | MTDB stored large soil stockpile directly over manhole | City rodded line/cleared blockage; MTDB diverted spill into sewer | N | N | Y | Alvarado Channel | SD River | Dog Beach via SD River | Y | N | N | N/A | 0
|  | City of La Mesa | City of La Mesa | 2003-11-23 12:00 | 2003-11-23 13:00 | 300 | 300 | BLOCKAGE | 03-4 | N/A | 11/23/03 12:00 | David Schoolcraft | 619-871-1613 | City of La Mesa | City of La Mesa | 11/23/03 12:00 | 11/23/03 13:00 | 5 | 300 | 300 | 0 | 8111 University Ave | La Mesa | 91941 | SD | 8 inch clay pipe | 0 | N/A | BLOCKAGE | Rags blocking line | Storm drain was flushed and vacuumed with water | N | Y | N | University Channel | Chollas Creek | Storm drain system | Y | N | N | N/A | 0
|  | City of Vista | PRIVATE PROPERTY | 2003-08-27 07:01 | 2003-08-28 13:00 | Unknown | 100 | Rocks | 034001 | faxed | 2003-08-28 15:13 | George Solano | (760) 726-1340, X-1661 | City of Vista | PRIVATE LATERAL | 2003-08-27 07:01 | 2003-08-28 13:00 | Unknown | Unknown | 100 | Unknown | 836 Sinkler Way | Vista | 92083 | SD | V28.129 | 3 | 10/22/2000; 01/29/2002; 03/13/2002 | Rocks | Rocks from surrounding parking area entered the private sewer lateral. Broken lateral as a result of improperly protected cleanout. | Wastewater division took no action -- private lateral; Storm Water division (Keri Martinez) was contacted. | N | Y | Unknown | Buena Vista Creek | Buena Vista Creek | N/A | Y | N/A | Y | At Melrose Drive | 4 | Private Sewer System
|  | Buena Sanitation District | PRIVATE PROPERTY | 2003-08-29 08:00 | 2003-08-29 09:30 | 90 | 90 | Unknown | 034002 | faxed | 2003-08-29 09:30 | Vactor crew | 760.726-1340 | City of Vista | PRIVATE LATERAL | 2003-08-29 08:00 | 2003-08-29 09:30 | 1 | 90 | 90 | None | 111 Palmyra Street | Vista | 92083 | SD | B09.56 | 0 | N/A | Unknown | Unknown | None by City of Vista | N | N | N | None | None | From Curb gutter to Vactor | Y | N/A | N | N/A | 0 | City crew responded to private lateral spill afer plumber cleaned the lateral. City crew washed down city right-of-way into vactor. The Stormdrain div. was notified.
|  | City of Vista | PRIVATE PROPERTY | 2003-09-08 12:30 | 2003-09-08 16:00 | 105 | 100 | Unknown | 034003 | faxed | 2003-09-08 12:25 | Jim Gusman/ George Solano | (760) 726-1340, X-1661 | City of Vista | PRIVATE LATERAL | 2003-09-08 12:30 | 2003-09-08 16:00 | 0.5 | 105 | 100 | Unknown | 941 E. Vista Way | Vista | 92084 | SD | V21.192 | 0 | N/A | Unknown | Unknown | City Stormwater officer (Sandy Sotola) issued citation. 760.726-1340, X1334. | N | Y | Unknown | Buena Vista Creek | None | Storm drains | Y | N/A | N | N/A | N/A | Private Sewer System
|  | City of Vista | City of Vista | 2003-09-15 22:00 | 2003-09-16 12:45 | 13275 | 1200 | Vandalism | 034004 | faxed | 2003-09-16 16:35 | Bob Milan | 760.726-1340 | City of Vista | City of Vista | 2003-09-15 22:00 | 2003-09-16 12:45 | 15 | 13275 | 1200 | 12075 | 247 E. Bobier Dr. | Vista | 92084 | SD | V14.088 | 0 | N/A | Vandalism | Vandals put large uncoiled sewer snake, motor, & frame… and other debris into the sewer manholes. | All debris was recovered after the blockage was broken; Manhole will be capped. | N | Y | Y | Storm drains | Buena Vista Creek | N/A | Y | Y | Y | Both sides of drainage between Cananea and Bobier. | 3 | Signs to remain for 72-Hr min. as required by San Diego County Health Dep't.
|  | City of Vista | PRIVATE PROPERTY | 2003-09-22 12:30 | 2003-09-22 16:20 | 345 | 100 | Grease | 034005 | faxed | 2003-09-23 08:40 | Bob Milan | 760.726-1340 | City of Vista | PRIVATE LATERAL | 2003-09-22 12:30 | 2003-09-22 16:20 | 1.5 | 345 | 100 | 175 | 525 W. Vista Way | Vista | 92084 | SD | V10.020 | N/A | N/A | Grease/ Roots | Blockage to private sewer system caused by heavy grease and roots. | Recommended routine cleaning of the private lateral line. | N | Y | Y | Buena Vista Creek | None | N/A | Y | N/A | N | N/A | N/A | Private Sewer System
|  | City of Vista | City of Vista | 2003-10-15 11:55 | 2003-10-15 12:02 | 70 | 35 | Roots | 034006 | faxed | 2003-10-15 11:55 | Bob Milam | 760.726-1340 | City of Vista | City of Vista | 2003-10-15 11:55 | 2003-10-15 12:02 | 10 | 70 | 35 | 35 | 656 Matagual | Vista | 92084 | SD |  | 0 | N/A | Roots | Roots blocking manhole in mainline downstream | Capture all roots from manhole that crew is working at | N | Y | N | None | None | Dried up in storm drain | Y | N/A | N | N/A | N/A | Long stretch of storm drain underground; no public access
|  | City of Vista | City of Vista | 2003-10-19 07:06 | 2003-10-19 07:36 | 30 | 30 | Grease | 034007 | faxed | 2003-10-21 10:30 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2003-10-19 07:06 | 2003-10-19 07:36 | 2 | 30 | 30 | 0 | Las Palmas at S. Melrose Dr. | Vista | 92083 | SD | V30.41 | 0 | N/A | Grease | Heavy grease used by residential area. | Continue to clean every line segment in this area at least once every 6-8 months. Also at every a product called 'DUKES' is being added to the cleaning truck to prevent grease buildup within sewer lines. | N | Y | N | None | None | Storm drains; approx. 1,000 lf of storm drain was vacuumed and washed. | Y | N/A | N | N/A | N/A | City crew vacuum and washed down sewage from road surface; the storm drain was also cleaned.
|  | City of Vista | City of Vista | 2003-12-05 08:30 | 2003-12-05 09:01 | 750 | 250 | Roots | 034008 | faxed | 2003-12-05 08:30 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2003-12-05 08:30 | 2003-12-05 09:01 | 25 | 750 | 250 | 500 | 1280 Tylee Street | Vista | 92083 | SD | V03.72 | 0 | N/A | Roots | Roots blocking city mainline possibly from private lateral. | Continue to clean every line segment in this area at least once every 6-8 months increasing our root control in this area; film line to find if improperly maintained private lateral caused blockage. | N | Y | N | None | None | Storm drain-recovered remainder at downstream storm drain | Y | N/A | N | N/A | N/A | City crew will follow up with downstream samples to be taken to Encina to the lab.
|  | City of Vista | City of Vista | 2003-12-05 09:20 | 2003-12-05 12:22 | 200 | 0 | Roots | 034009 | faxed | 2003-12-05 15:30 | Jim Gusman | 760.726-1340 | City of Vista | City of Vista | 2003-12-05 09:20 | 2003-12-05 12:22 | 1 | 200 | 0 | 200 | 1122 Vista Bonita Road | Vista | 92083 | SD |  | 0 | N/A | Roots | Root blockage near residents cleanout (heavy roots); no access to MH; lots of dogs in area creating a dangerous environment. Spill was saturated into a dry creek bed with no access. | City mainline will be televised to find cause of spill & to see if there are roots in the mainline. | N | N | N | None | None | Dry creek bed | Y | N/A | N | N/A | N/A | Application of Duke's root control will be performed at this line segment.
|  | City of Vista | City of Vista | 2003-12-22 07:00 | 2003-12-22 07:17 | 51 | 51 | Roots | 034010 | faxed | 2003-12-22 09:20 | Bob Milam | 760.726-1340 | City of Vista | City of Vista | 2003-12-22 07:00 | 2003-12-22 07:17 | 3 | 51 | 51 | 0 | 1023 Oak Drive | Vista | 92084 | SD |  | 0 | N/A | Roots | Root blockage; need to televise line to determine whether blockage was caused from a private lateral or city mainline. | Root cut line; put line segment on a hot spot list | N | Y | N | None | None | Storm drain; vacuumed out storm drain | Y | N/A | N | N/A | N/A | Total capture of overflow & rinsed down street & storm drain.
|  | El Toro Water District | El Toro Water District | 2003-11-04 06:00 | 2003-11-04 09:26 | 1030 | 20 | UNKNOWN | 023002 | Brian Kelly | 2003-11-04 | Renzo Marin | (949) 837-7050 | El Toro Water District | El Toro Water District | 2003-11-04 06:00 | 2003-11-04 09:26 | 5 | 1030 | 20 | 1010 | 24782 Leto Circle | Mission Viejo | 92691 | OC | ETWD Atlas page MD- 507, MH #2 | 0 | N - A | UNKNOWN | Cause of blockage was unknown | Set up containment area with sand bags in front of storm drain. Used Vactor/Hydro cleaner truck to break blockage and vacuum contained spill. Cleaned, washed down, and vacuumed wash down water. TV Video inspection showed line to be in good conditions | Y | Y | Y | Storm drain | Oso Creek | Oso Creek | Y | Y | Y | By OCHD |  | Notified all Regulatory agencies, City of MV and emailed Pictures and Report. This line was last cleaned July 2002.
|  | El Toro Water District | El Toro Water District | 2003-11-15 11:36 | 2003-11-15 13:45 | 258 | 164 | UNKNOWN | 023003 | Victor Vasquez | 2003-11-15 | Renzo Marin | (949) 837-7050 | El Toro Water District | El Toro Water District | 2003-11-15 11:36 | 2003-11-15 13:45 | 2 | 258 | 164 | 94 | 908 Rhonda Sevilla | Mission Viejo | 92691 | OC | ETWD Atlas page MF- 496, MH #17 | 0 | N - A | UNKNOWN | Cause of blockage was unknown | Set up containment area with sand bags and sand tubes to block water from entering the catch basin. Used Hydro cleaner and Mini Jetter to break blockage. Overflow manhole located in very large landscaped area, all contained water was absorbed by ground surroundings. District staff still investigating overflow occurrence. This site is on the Hot Spots list and is on a bimonthly cleaning schedule. Further mitigation measures may be implemented once the investigation is completed | Y | Y | Y | Storm drain | Aliso Creek | Aliso Creek | Y | N | N | N/A |  | Notified all Regulatory agencies, City of MV and emailed Pictures and Report. This line was last cleaned September 2003
|  | El Toro Water District | El Toro Water District | 2003-12-13 13:45 | 2003-12-13 14:15 | 180 | 90 | GREASE | 023004 | Victor Vasquez | 2003-12-13 | Renzo Marin | (949) 837-7050 | El Toro Water District | El Toro Water District | 2003-12-13 13:45 | 2003-12-13 14:15 | 3 | 180 | 90 | 90 | 23354 Muirlands | Lake Forest | 92630 | OC | 23354 Muirlands Private Manhole | 0 | N - A | GREASE | Grease blockage downstream of manhole | Set up containment area with sand tubes and dirt. Used Vactor to vacuum up spill while using Hydro cleaner to break blockage. Washed down area, recovered all contained sewage, wash down water and contaminated dirt. Communicating with IRWD regarding grease control at various restaurants in shopping center. Shopping center is in IRWD service area but drains to ETWD sewer system. | N | Y | Y | Storm drain | Aliso Creek | Aliso Creek | Y | N | N | N/A |  | Notified all Regulatory agencies, City of MV and emailed Pictures and Report. ETWD line was last cleaned March 2002, TV July 2003. Blockage was in shopping center lateral.
|  | Fallbrook Public Utilities District | PRIVATE PROPERTY | 07/17/2003 13:20 | 07/17/2003 14:30 | 1200 | 500 | PRIVATE PROPERTY | 034001 | FAX 858-571-6972 | 06/17/2003 15:45 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | PRIVATE LATERAL | 07/17/2003 13:20 | 07/17/2003 14:30 | 17 | 1200 | 500 | 700 | 525-605 Alturas Road | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Grease in apartment's private lateral. | Flush truck on site, flushed lateral and washed down parking lot and vactored water. | N | Y | N | None. | None. | Storm drain. | Y | N | N |  | 0 | COURTESY NOTIFICATION
|  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 07/29/2003 11:50 | 07/29/2003 12:15 | 25 | 25 | ROOTS | 034002 | QUARTERLY REPORT |  | Joel V. Holt | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 07/29/2003 11:50 | 07/29/2003 12:15 | 1 | 25 | 25 | 0 | 763 Carnation Lane | Fallbrook | 92028- | SD | Manhole | 0 |  | ROOTS | Roots in mainline. | Flushed mainline and opened at 162 feet. Flushed mainline second time to clean for CCTV. Will CCTV within 24 hours. Removed roots from upper mahole walls. Removed dirt from around manhole. | N | N | N | None. | None. | Soaked into dirt around manhole. | N | N | N |  | 0 | Manhole was not flowing when we arrived. Spill had soaked into dirt around manhole. Removed dirt that was contaminated. Put copper sulfate on roots in manhole.
|  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 08/13/2003 06:30 | 08/13/2003 08:30 | 3000 | 2000 | LINE BREAK | 034003 | FAX 858-571-6972 | 08/13/2003 12:25 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 08/13/2003 06:30 | 08/13/2003 08:30 | 25 | 3000 | 2000 | 1000 | 2857 S. Mission Road | Fallbrook | 92028- | SD | 10" Force Main on Overland Trail | 2 | 10-29-02, 10-30-02 | LINE BREAK | 10" force main from Overland Trail Pump Station | Shut pump station down and opened valve to overflow tank. | N | N | Y | Ostrich Creek | San Luis Rey River, Pacific Ocean | Did not reach secondary waters. Vactored out of Ostrich Creek about 1/8 mile downstream of overflow location. | Y | Y | Y | Along Creek | 3 | Located leak and re-sectioned broken pipe. Removed contaminated dirt. Vactored spill from creek at about 1/8 mile downstream. Spill never reached secondary waters. Estimate 2400 gallons went to creek. Vactored a total of 8,000 gallons from creek. FPUD has repeatedly offered to the RWQCB to divert all low flow in Ostrich Creek to treatment. The RWQCB has rejected this offer.
|  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 09/04/2003 12:15 | 09/04/2003 12:45 | 150 | 0 | UNKNOWN | 034004 | QUARTERLY REPORT |  | Joel V. Holt | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 09/04/2003 12:15 | 09/04/2003 12:45 | 5 | 150 | 0 | 150 | 952 Tanya Lane | Fallbrook | 92028- | SD | Manhole | 0 |  | UNKNOWN | Found paper towels and roots. | Flushed mainline, found stoppage at 374 feet. | N | N | N | None. | None. | In rear of the house in the yard. | Y | N | N |  | 0 | Soaked into ground. Disinfected ground.
|  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 10/06/2003 07:10 | 10/06/2003 08:00 | 50 | 50 | ROOTS | 034005 | QUARTERLY REPORT |  | Joel V. Holt | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 10/06/2003 07:10 | 10/06/2003 08:00 | 1 | 50 | 50 | 0 | 900 block Pizzo Lane | Fallbrook | 92028- | SD | Manhole | 0 |  | ROOTS | Roots in mainline. | Flushed mainline stoppage at 375 feet. | N | N | N | None. | None. | Alongside of road and puddled up. | Y | N | N |  | 0 | Stoppage at 375 feet cleared. Used clean up water and vactored up.
|  | Fallbrook Public Utilities District | PRIVATE PROPERTY | 12/04/2003 14:30 | 12/04/2003 14:45 | 30 | 25 | PRIVATE PROPERTY | 034006 | FAX 858-571-6972 | 12/05/2003 13:45 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | PRIVATE PROPERTY | 12/04/2003 14:30 | 12/04/2003 14:45 | 2 | 30 | 25 | 5 | 1510 S. Mission Road | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Grease and food particles. | Rodded and vacuumed up overflow. Washed down area and vacuumed wash down water. | N | Y | N | None. | None. | Storm drain. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Damned up overflow before major flow entered storm drain.
|  | City of Laguna Beach | PRIVATE PROPERTY | 2003-07-21 11:00 | 2003-07-23 11:15 | 50 | 45 | Line Break | 034001 | Fax | 2003-07-23 15:38 | David Shissler | (949) 497-0719 | City of Laguna Beach | City of Laguna Beach | 2003-07-21 11:00 | 2003-07-23 11:15 | 3.33 | 50 | 45 | 5 | 2790 Queda Way | Laguna Beach | 92651 | OR | Sewer Injector Pump | 0 |  | Line Break | We received a call from Andrus Plumbing alerting us of a private sewer spill at 2790 Queda Way. Sewer crews arrived on scene and found that the injector pumps that serviced this location had failed due to a separation of the discharge pipe. The unsupported piping caused the clamps to separate under head pressure which released sewage into the area around the sewer pump. | Andrus Plumbing replaced all piping clamps and added support bracing to the pump discharge pipe. City staff did a follow-up inspection to ensure that the necessary repairs had been completed. | N | N | N | N/A | N/A | The overflow was contained and pumped into the City's vacuum truck. Approximately 5 gallons evaporated into the dirt area. | Yes | No
|  | City of Laguna Beach | City of Laguna Beach | 2003-08-15 14:40 | 2003-08-15 15:00 | 10 | 1 | Roots | 034002 | Victor Vasquez | 2003-08-15 15:40 | Bernadette McCusker | (949) 497-0342 | City of Laguna Beach | City of Laguna Beach | 2003-08-15 14:40 | 2003-08-15 15:00 | 0.5 | 10 | 1 | 9 | 408 Panorama Drive | Laguna Beach | 92651 | OR | Manhole C21-018 | 3 | 8/19/02, 3/24/03, 5/19/03 | Roots | The Sewer Division received a call at 14:40 from Jay Lenker who is the resident at 408 Panorama Drive. He stated that there was a manhole trickling over in front of his residence. Sewer crews responded and arrived at 14:50. They observed that the manhole was trickling over. The apparent cause of overflow was roots originating from a private lateral. | Sewer crews proceeded to the downstream manhole, set up the rodder truck and sanbagged around the storm drain. They rodded from the upstream manhole and cleared a root ball which had been pushed down from a private lateral. | N | Y | N | Storm Drain | N/A | Vacuumed up all overflow into the vacuum truck | Yes | No |  |  |  | The overflow entered the storm drain catch basin only. All leaves and debris were swept up into the vacuum truck. The main line was video inspected on August 15, 2003. The inspection confirmed that the pipe was lined and was operating without any main line root intrusion. As of November 21, 2002, the entire upstream portion of the collection system has been lined or was televised and determined to be in good service condition.
|  | City of Laguna Beach | City of Laguna Beach | 2003-09-20 10:40 | 2003-09-20 10:45 | 3 | 2 | Roots | 034003 | Fax | 2003-09-23 15:30 | David Shissler | (949) 497-0719 | City of Laguna Beach | City of Laguna Beach | 2003-09-20 10:40 | 2003-09-20 10:45 | 0.6 | 3 | 2 | 1 | 1542 Santa Cruz | Laguna Beach | 92651 | OR | Manhole F24-156 | 1 | 2003-01-26 | Roots | The Water Quality Department received a call from Laguna Beach Police Department at 10:40 a.m. They stated that they had received a call from the resident at 1542 Santa Cruz. The resident stated that sewage was trickling out from the manhole in her driveway. Upon arriving at the location, the leaking was observed to have stopped and the manhole was found to be surcharged. | Crews set up and jetted from the downstream manhole #F24-156 up to manhole #F24-164. The blockage was cleared after removing a large ball of roots from the sewer line. | N | N | N | N/A | N/A | Vacuumed up the majority of the spill into the City's vactor truck | Yes | No |  |  |  | Trace amounts soaked into the ground around the landscaping and the remainder evaporated. As a precaution, City crews washed down the driveway and vacuumed up all excess water into the vactor truck.
|  | City of Laguna Beach | PRIVATE PROPERTY | 2003-09-30 13:10 | 2003-09-30 13:10 | 15 | 10 | Debris | 034004 | Email | 2003-10-02 16:00 | David Shissler | (949) 497-0719 | City of Laguna Beach | City of Laguna Beach | 2003-09-30 13:10 | 2003-09-30 13:10 | 15 | 15 | 10 | 5 | 2856 Terry Road | Laguna Beach | 92651 | OR | Private Cleanout |  |  | Debris | We received a call from the resident at 2859 Terry Road who stated that the cleanout at 2856 Terry Road was overflowing. We arrived on scene and found that the overflow had stopped, but had reached the storm drain. | We vacuumed up the storm drain and jetted the main line which found to be clear. The downstream storm drains were checked and found to be completely dry. We then informed the property owner not to use any water and to call a plumber for repairs. A follow up was done the next day and repairs had been completed. | N | Y | N | Storm Drain | N/A | The majority of the spill was recovered by the Vactor truck. The remainder soaked into the ground and evaporated. | Yes | No |  |  |  | The majority of the spill was recovered by the Vacuum truck. The remainder soaked into the ground and evaporated.
|  | City of Laguna Beach | PRIVATE PROPERTY | 2003-10-14 15:30 | 2003-10-14 15:52 | 20 | 19 | Debris | 034006 | Email | 2003-10-16 15:45 | David Shissler | (949) 497-0719 | City of Laguna Beach | City of Laguna Beach | 2003-10-14 15:30 | 2003-10-14 15:52 | 0.9 | 20 | 19 | 1 | 910 North Coast Hwy | Laguna Beach | 92651 | OR | Private Sewer Lateral | N/A | N/A | Debris | Laguna Beach Police Dispatch notified staff of a sewer problem in the 900 blk. Of North Coast Hwy at 3:42 p.m. Staff arrived and determined that the private lateral from 910 N. Coast Hwy was leaking. | Fire personnel built a dam to prevent the overflow from entering the storm drain. We jetted the main line and sandbagged around the cleanout. We then washed down the sidewalk and vacuumed up all water into the vacuum truck. We advised the businesses not to use any water and contacted the property owner to call a plumber as soon as possible. A follow-up was done the next morning and all repairs had been made | N | N | N | N/A | N/A | Pumped back into the vacuum truck. The remainder soaked into the ground | Y | N | N | N/A | N/A
|  | City of Laguna Beach | PRIVATE PROPERTY | 2003-12-22 09:00 | 2003-12-22 11:10 | 25 | 24.99 | Roots | 034007 | Email | 2003-12-29 10:00 | David Shissler | (949) 497-0719 | City of Laguna Beach | City of Laguna Beach | 2003-12-22 09:00 | 2003-12-22 11:10 | 0.19 | 25 | 24.99 | 0.01 | 294 Cortez | Laguna Beach | 92651 | OR | Private Sewer Lateral | N/A | N/A | Roots | City staff were called by Mike Phillips from City Hall in reference to a possible private sewer overflow at 2094 Cortez. Staff arrived on scene and found that the overflow had trickled into the storm drain but had stopped. Rescue Rooter was on scene and | Rescue Rooter were snaking the line when City staff arrived on scene. Staff sandbagged the storm drain box downstream of this location and washed down the area and vacuumed the water into the Aquatech. | N | Y | N | Storm Drain | N/A | Pumped back into the vacuum truck. The remainder soaked into the ground | Y | N | N | N/A | N/A
|  | City of Laguna Beach | City of Laguna Beach | 2003-11-26 23:50 | 2003-11-27 00:15 | 10 | 0 | Debris | 034008 | Phone | 2003-11-28 | David Shissler | (949) 497-0719 | City of Laguna Beach | City of Laguna Beach | 2003-11-26 23:50 | 2003-11-27 00:15 | 0.4 | 10 | 0 | 10 | 1555 Catalina | Laguna Beach | 92651 | OR | 8-inch City Main Line | 0 | N/A | Debris | Laguna Beach Police Dispatch notified Water Quality Staff of a possible sewer backup at 1555 Catalina Street. Staff responded and determined that the 8 inch City sewer main line was plugged. This plugged line resulted in sewage backing up into the crawl space underneath the house at 1555 Catalina Street. | Staff used the Aquatech to clear the stoppage from Manhole #F25-051. A follow up cleaning to the main line was performed on the morning of November 27th and a large piece of concrete was removed from the line. | N | N | N | N/A | N/A | Soaked into the dirt in the crawl space underneath the house. | Y | N | N | N/A | N/A
|  | Moulton Niguel Water District | Moulton Niguel Water District | 2003-11-14 13:30 | 2003-11-14 15:00 | 1800 | 1800 | Roots | 034001 | FAX (858) 571-6972 | 2003-11-14 16:30 | Brad Bruington | (949) 425-3543 | Moulton Niguel Water District | Moulton Niguel Water District | 2003-11-14 13:30 | 2003-11-14 15:00 | 20 | 1800 | 1800 | 0 | Via Angelina & Via Casitas | Mission Viejo | 92691 | OR | 10" VCP Sewer | 0 | 0 | Roots | Cracked bell top of 10" VCP pipe at beginning of encasement. Roots entered damaged pipe to cause root blockage. | Pipe line was repaired and concrete placed at joints to stop root intrusion. | Y | N | Y | Oso Creek | Upper Oso RW res & sewer | See remarks | Y | Y | N | None | 0 | Overflow and stream water was pumped out of creek at Upper Oso creek barrier and pumped to SMWD's Zone B Pump Station. Initially, pump station pumped to Upper Oso Reservoir until Zone B Pump Station was turned off. Flow entered Oso Trabuco sewer trunk sewer.
|  | City of Oceanside | City of Oceanside | 07/10/03 0805 | 07/10/03 0850 | 180 | 0 | ROOTS | 034001 | Quarterly Report |  | Michael Heiser | 7604355870 | City of Oceanside | City of Oceanside | 07/10/03 0805 | 07/10/03 0850 | 4 | 180 | 0 | 180 | 3124 Camino Crest Drive | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots were primary cause, grease also contributed. | Line was rodded and jetted. | N | N | N | None | None | Soaked into #12 Fairway at El Camino Golf Course | Y | N | N |  |  | Line will also be televised.
|  | City of Oceanside | City of Oceanside | 08/07/03 2230 | 08/08/03 0630 | 1500000 | 1500000 | LINE BREAK | 034002 | Victor Vasquez | 08/08/03 1054 | Guss Pennell | 7604355804 | City of Oceanside | City of Oceanside | 08/07/03 2230 | 08/08/03 0630 | 3125 | 1500000 | 1500000 | 0 | 3950 North River Road | Oceanside | 92054 | SD | 24" Force Main @ SLR WRF | 1 | 2003-03-16 | LINE BREAK | Influent line failed prior to planned bypass. Cause at this time is unknown. | Flow has been diverted into another line. Replaceing section that failed. | N | N | N | None | None | Entire flow was diverted into pipe gallery at WRF. Flow was then pumped into treatment process. | Y | Y | N |  |  | O&M personnel & contractor's crew preparing to tie-in flow to new 24" and 36" influent lines. Existing 24" line, aprox. 100 ft. south of tie-in, failed. Patch was applied, but failed also. Flow was divered at up stream pump station into 42" line until repairs can be made.
|  | City of Oceanside | City of Oceanside | 08/08/03 1400 | 08/08/03 2400 | 441000 | 11000 | LINE BREAK | 034003 | Victor Vasquez | 08/08/03 1502 | Guss Pennell | 7604355804 | City of Oceanside | City of Oceanside | 08/08/03 1400 | 08/08/03 2400 |  | 441000 | 11000 | 430000 | 3476 Mission Avenue | Oceanside | 92054 | SD | Manholes & diversion pipeline. | 0 |  | LINE BREAK | 24" Influent line at SLR WRF failed, causing sewerage to back up within collection system. | Flow was diverted into 42" line from B.V. pump station. Flows diverted away from B.V. pump station into Encina Collection System. | N | Y | N | None | None | Overflow soaked into earthern Flood Control Detention Basin, where contained and evaporated. | Y | Y | N |  |  | Additional details are too voluminous for this cell. Please refer to hard copy of report which has been faxed to all regulatory agencies.
|  | City of Oceanside | City of Oceanside | 08/13/03 1400 | 08/13/03 1405 | 5 | 5 | BLOCKAGE | 034004 | Quarterly Report |  | David Sanchez | 7608011178 | City of Oceanside | City of Oceanside | 08/13/03 1400 | 08/13/03 1405 | 1 | 5 | 5 | 0 | 2315 Rancho Del Oro | Oceanside | 92054 | SD | Manhole | 0 |  | BLOCKAGE | Grease blocked line. | Line was jetted to clean it. | N | Y | N | None | None | Flow puddled into dirt of storm drain box. | Y | Y | N
|  | City of Oceanside | PRIVATE PROPERTY | 08/30/03 1413 | 08/30/03 1735 | 808 | 775 | OTHER | 034005 | Voice Mail | 08/30/03 1902 | Michael Heiser | 7604355870 | City of Oceanside | City of Oceanside | 08/30/03 1413 | 08/30/03 1735 | 4 | 808 | 775 | 33 | 415 Grant Street | Oceanside | 92054 | SD | Apt. Cleanout | 0 |  | OTHER | Cleanout cap was off at Apt.Bldg. Unk. Debris in line. | Plumbing company broke stoppage. Line was jetted twice. | N | Y | Y | Loma Alta Creek | None |  | Y | N | Y |  |  | Runoff in gutter was vactored up at storm drain basin. Standing water in Loma Alta Creek, but little flow. Gutter washed with hydrant.
|  | City of Oceanside | City of Oceanside | 09/06/03 1000 | 09/06/03 1020 | 20 | 0 | DEBRIS | 034006 | Quarterly Report |  | Tom Lujan | 7604355870 | City of Oceanside | City of Oceanside | 09/06/03 1000 | 09/06/03 1020 | 1 | 20 | 0 | 20 | 3190 Vista Way | Oceanside | 92056 | SD | Manhole | 0 |  | DEBRIS | Unknown debris caused partial stoppage. | Line was jetted twice. | N | N | N | None | None | All evaporated from curb and gutter. | Y | N | N
|  | City of Oceanside | City of Oceanside | 09/09/03 1045 | 09/09/03 1145 | 780 | 500 | BLOCKAGE | 034007 | Voice Mail | 09/09/03 1723 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 09/09/03 1045 | 09/09/03 1145 | 13 | 780 | 500 | 280 | Industry St. & Garrison St. | Oceanside | 92054 | SD | Manhole | 0 |  | BLOCKAGE | Construction Material blocked line and covered deck of two manholes. | City is aggressively investigating the incident to establish the orgin of the blockage. Area is maintained by vactor . Sending CCTV out to film pipe condition. | N | Y | Y | Garrison Flood Control Channel | Loma Alta Creek |  | Y | N | N |  |  | Stoppage lasted several hours. Spill was contained and bypassed back into sewer system. Two manhole entries required to remove large amount of construction material. Spill never reached ocean because Loma Alta Creek dammed at Buc. Beach.
|  | City of Oceanside | City of Oceanside | 09/28/03 1730 | 09/28/03 1810 | 40 | 0 | ROOTS | 034008 | Voice Mail | 09/29/03 0740 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 09/28/03 1730 | 09/28/03 1810 | 1 | 40 | 0 | 40 | Skyhaven & Lake Blvd. | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Root intrusion caused grease buildup. | Line is jetted routinely and will be scheduled for CCTV. | N | Y | Y | Buena Vista Creek | None |  | Y | N | N |  |  | Spill started on Skyhaven, traveled down Lake Blvd. Into storm drain which daylights into nearby Buena Vista Creek. Limited access prevented recoverfy.
|  | City of Oceanside | City of Oceanside | 10/03/03 1350 | 10/03/03 1410 | 60 | 0 | DEBRIS | 034009 | Victor Vasquez | 10/03/03 1528 | Michael Heiser | 7604355870 | City of Oceanside | City of Oceanside | 10/03/03 1350 | 10/03/03 1410 | 3 | 60 | 0 | 60 | 3600 Vista Campana North | Oceanside | 92054 | SD | Manhole | 0 |  | DEBRIS | Line has offset joint. Debris and grease build up around it and cause stoppage. | Line was jetted and is on a replacement list to be moved up onto the roadway where it is accessable. | N | Y | N | None | None | Open scrub brush area where storm drain "daylights". | Y | N | N |  |  | Spill soaked into open land. No access to easement for recovery.
|  | City of Oceanside | City of Oceanside | 10/20/03 1000 | 10/20/03 1110 | 6580 | 6580 | CONSTRUCTION | 034010 | Victor Vasquez | 10/20/03 1130 | Mark Anderson | 7604355960 | City of Oceanside | City of Oceanside | 10/20/03 1000 | 10/20/03 1110 | 94 | 6580 | 6580 | 0 | 3950 North River Road | Oceanside | 92054 | SD | Force Main | 1 | 2003-08-08 | CONSTRUCTION | Heavy construction broke off underground 1-inch fitting attached to 42-inch force main. | Steel plate was welded over the 1-inch opening. | N | N | N | None | None | Sewage returned to headworks. | Y | Y | N |  |  | See attached digital photos for visual explanations.
|  | City of Oceanside | PRIVATE PROPERTY | 11/26/03 1235 | 11/26/03 1309 | 102 | 102 | PRIVATE PROPERTY | 034011 | Quarterly Report |  | Mike Heiser | 7604355870 | City of Oceanside | City of Oceanside | 11/26/03 1235 | 11/26/03 1309 | 3 | 102 | 102 | 0 | 3770 Mission Avenue | Oceanside | 92054 | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Plumber broke stoppage. | Not Applicable | N | Y | N | None | None | Storm Drain | Y | N | N |  |  | Storm drain cleaned out by City Vactors.
|  | City of Oceanside | City of Oceanside | 11/29/03 1253 | 11/29/03 1329 | 72 | 72 | ROOTS | 034012 | Voice Mail | 11/29//03 1357 | Mike Heiser | 7604355870 | City of Oceanside | City of Oceanside | 11/29/03 1253 | 11/29/03 1329 | 2 | 72 | 72 | 0 | 2165 Calle Buena Ventura | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots coming into Grade Rings | Manhole cleaned of roots and turned over to management for manhole refinishing. | N | Y | N | None | None | Storm Drain | Y | N | N |  |  | Vactor broke stoppage. WrkOrdr requested manhole be refinished..
|  | City of Oceanside | City of Oceanside | 11/29/03 1719 | 11/29/03 1933 | 670 | 0 | ROOTS | 034013 | Voice Mail | 11/29/03 2150 | Tom Lujan | 7604355870 | City of Oceanside | City of Oceanside | 11/29/03 1719 | 11/29/03 1933 | 5 | 670 | 0 | 670 | 3066 Sonja Court | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots & rags caused stoppage. | Line was rodded and will be TV'd. | N | N | N | None | None | Soaked into homeowners ground. | Y | N | N |  |  | No recovery was possible due to soaking into ground.
|  | City of Oceanside | City of Oceanside | 12/15/03 1905 | 12/15/03 1953 | 960 | 600 | GREASE | 034014 | Voice Mail | 12/15/03 1710 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 12/15/03 1905 | 12/15/03 1953 | 20 | 960 | 600 | 360 | 161 Thunder Drive | Oceanside | 92054 | SD | Manhole | 0 |  | GREASE | Grease blocking City Main | Chased spill downstream to insure debris did not backup again. Dropped Chlorine upstream to burn leftover grease. | Y | Y | Y | Buena Vista Creek | Buena Vista Lagoon |  | Y | N | N |  |  | EnvHealth said posting not necessary.
|  | Rainbow Municipal Water District | PRIVATE PROPERTY | 2003-08-21 | 2003-08-21 | 500 | 50 | GREASE | 034001 | VOICEMAIL | 2003-08-21 23:00 | Ramon Zuniga | (760) 728-1178 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2003-08-21 | 2003-08-21 | 0 | 500 | 50 | 450 | 31505 Old River Road | Bonsall | 92003 | SD | nearest MH is 28F-M100 | 0 | 0 | GREASE | Cause of SSO appeared to be grease related. Upon arrival to Bonsall School District noticed heavy debris on asphalt ground. | Responded to sewer spill at Bonsall School grounds, contained area and set up warning signs to keep people away from sewer spill. Notified Regulatory Agencies County Environmental Health Clay Clifton, RWQCB Victor Vasquez and County Hazmat of incident. Scraped up 50 gallons of debris and disinfected area and barricaded parking lot. Note: Based on Superintendant conversation there have been spills at this location before. | N | N | N | None | None | Bonsall School parking lot and Old River Road | Y | N | Y | North side of Old River Road, Bonsall CA | 1 | This is a private sewer lateral that spilled on 8/21/03. RMWD was notified by North County Fire Department Fire Captain Mike Bungrez. Rainbow Municipal Water District is not responsible for maintenance of this private sewer lateral.
|  | City of San Clemente | City of San Clemente | 2003-07-27 08:46 | 2003-07-27 09:50 | 320 | 50 | DEBRIS | 034001 | Fax | 2003-07-27 13:00 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-07-27 08:46 | 2003-07-27 09:50 | 5 | 320 | 50 | 270 | Via Montana & Pastadero | San Clemente | 92672 | OC | 8" Gravity | 0 | 0 | DEBRIS | Gritl, dirt and rag build up in the 8" main line | Placed on a quaterly cleaning schedule | n | y | y |  |  | Pacific Ocean | y | n | y | North Beach in San Clemente | 5
|  | City of San Clemente | City of San Clemente | 10-26-03 10:15am | 10-26-03 11:00am | 16156 | 16156 | POWER FAILURE | 034002 | FAX | 10-26-03 4:30pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 10-26-03 10:15am | 10-26-03 11:00am | 360 | 16156 | 16156 | 0 | 390 Ave. Pico | San Clemente | 92672 | OC | Sewage Pump Station | 0 | 0 | POWER FAILURE | Power Failure, Back-up Generator Failed | Reapired Generator Unit | n | y | n | MO2 County Flood Control | None | Returned to the sewer system | y | y | n
|  | City of San Clemente | PRIVATE PROPERTY | 10/28/2003 9:10am | 10-28-03 9:40am | 60 | 20 | BLOCKAGE |  | FAX | 10-28-03 2:00pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 10/28/2003 9:10am | 10-28-03 9:40am | 2 | 60 | 20 | 40 | 1407 Buena Vista | San Clemente | 92672 | OC | Private Lateral | 0 | 0 | BLOCKAGE | Private Lateral | Water shut off until repairs are completed | n | y | y | None | None | Pacific Ocean | y | n | y | 204 Beach in San Clemente | 3
|  | County of San Diego | County of San Diego | 2003-09-13 10:30 | 9/13/03 - 1130 | 1800 | 0 | VANDALISM | 034002 | VOICE MAIL 571-6922 | 9/15/03 0645 | BILL WILTSE | 619-660-2007 | Co. SD | Co.SD | 9/13/03 - 1030 | 9/13/03 - 1130 | 30 | 1800 | 0 | 1800 | 1020 GILLESPI ST. | SPRING VALLEY | 91978 | SD | 584-512-332B | 0 | NA | VANDALISM | BASKETBALL AND OTHER DEBRIS IN LINE | CLEANED AND INSTALLED LOCKING LID | N | N | N | NA | NA | PRIVATE PROPERTY - GRASSLAND | Y | Y | N | NA | 0
|  | South Coast County Water District | South Coast County Water District | 2003-07-11 07:50 | 2003-07-11 08:20 | 250 | 250 | LINE BREAK | 034001 | FAX 858-571-6972 | 2003-07-11 07:50 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-07-11 07:50 | 2003-07-11 08:20 | 5 | 250 | 250 | 0 | 27032 Calle Delores | Capistrano Beach | 92624 | OC | MANHOLE #494 | 0 | NONE | LINE BREAK | After the lines were jet cleaned, crews did a video inspection of the sewer lines in the area and found broken sections with the most severe section being upstream of the manhole | Contractor was hired to excavate and replace the sewer pipe sections | N | Y | N | n/a | n/a | DOWNSTREAM CATCH BASIN | Y | N | N | n/a | 0 | 40 gallons of overflow was recovered at spill site, remainder was recovered from furthest downstream catch basin which is on PCH, no sewage reached beach or receiving waters
|  | South Coast County Water District | South Coast County Water District | 2003-07-23 06:00 | 2003-07-23 06:45 | 675 | 675 | BLOCKAGE | 034002 | FAX 858-571-6972 | 2003-07-23 13:50 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-07-23 06:00 | 2003-07-23 06:45 | 15 | 675 | 675 | 0 | 4230 Copper Lantern | Dana Point | 92629 | OC | MANHOLE #242 | 0 | NONE | BLOCKAGE | Blockage in sewer main (roots) caused by lateral cleaning | Crew jetted line to clear blockage. Ran root cutter and tv'd line to make certain line was clear. | N | Y | N | n/a | n/a | City of Dana Point storm water diversion structure located at PCH/Dana Point Harbor Dr | Y | N | N | n/a | 0 | SCWD pumped out stormwater diversion facility and stormwater at drainage ditch. No sewage reached beach or receiving waters
|  | South Coast County Water District | South Coast County Water District | 2003-08-10 15:26 | 2003-08-10 16:40 | 148 | 148 | BLOCKAGE | 034003 | FAX 858-571-6972 | 2003-08-11 16:14 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-08-10 15:26 | 2003-08-10 16:40 | 2 | 148 | 148 | 0 | 26962 Calle Dolores | Capistrano Beach | 92624 | OC | RESIDENTIAL CLEANOUT/ LATERAL | 1 | 2003-07-11 | BLOCKAGE | Overflow came from private lateral located in driveway. Crews inspected and jetted sewer main and found sediment/debris | Sewer line was jetted two times and vacuumed and video inspected by maintenance crews. Also, private sewer laterals on Calle Dolores and Calle Verano were inspected. | N | Y | N | n/a | n/a | STORM DRAIN | Y | N | N | n/a | 0 | Hired contractor to rebuild manhole #494 bottom where sediment was suspected to originate
|  | South Coast County Water District | PRIVATE PROPERTY | 2003-08-16 13:00 | 2003-08-16 13:30 | 300 | 0 | GREASE | 034004 | FAX 858-571-6972 | 2003-08-18 16:00 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-08-16 13:00 | 2003-08-16 13:30 | 10 | 300 | 0 | 300 | 25135 Park Lantern | Dana Point | 92629 | OC | LATERAL LINE | 0 | NONE | GREASE | Private plumber snaked service lateral to unclog problem | District will work with Marriott Hotel to address future grease problems | N | Y | Y | Dana Point Harbor | Pacific Ocean | n/a | Y | N | Y | From F to O Dock on the North side of east basin | 3 | Private System Overflow
|  | South Coast County Water District | PRIVATE PROPERTY | 2003-08-22 11:20 | 2003-08-22 13:30 | 0 | 0 | BLOCKAGE | 034005 | FAX 858-571-6972 | 2003-08-27 14:00 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-08-22 11:20 | 2003-08-22 13:30 |  |  |  |  | 34150 Pacific Coast Highway | Dana Point | 92629 | OC | LATERAL LINE | 0 | NONE | BLOCKAGE | Overflow came from private lateral from a restaurant. District was not notified of the original spill by restaurant owner. On 8/22/03 the City of Dana Point Code Enforcement Officer notified the District of a problem. When District crew spoke to the manager he indicated that there had been a spill approx. 2-3 weeks ago and that his guys cleaned up the area the best they could do without washing down the excess water into the storm drain. | When District crew arrived sewer backup was dried-up. District crew washed down and vacuumed up the residual sewage spill and spoke with the manager of the restaurant to correct overflow problem. District reported problem to the City of Dana Point Code Enforcement Officer. | N |  | *N | unknown | unknown | PARKING LOT UNDER RESTAURANT BUILDING | Y | N | N | n/a | 0 | *Private System Overflow. Because of the time frame of the spill, the overflow amouont is unknown and location of where it ended up is unknown, although there was no apparent release to any storm drains or receiving waters
|  | South Coast County Water District | South Coast County Water District | 2003-08-21 16:20 | 2003-08-21 21:00 | 25 | 25 | OTHER | 034006 | FAX 858-571-6972 | 2003-08-28 09:30 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-08-21 16:20 | 2003-08-21 21:00 | 0.1 | 25 | 25 | 0 | 24587 Santa Clara | Dana Point | 92629 | OC | RESIDENTIAL CLEANOUT/ LATERAL | 0 | NONE | OTHER | Private lateral not connected to newly constructed main | Contractor connected lateral to the new main. SCWD crews pumped approx 5000 gallons of sewage out of the old main and sealed old lateral connection with concrete slurry | N | N | N | n/a | n/a | CONTAINED IN CLEANOUT BOX AND FLOWER BED | Y | N | N | n/a | 0 | No sewage reached storm drain or receiving waters
|  | South Coast County Water District | PRIVATE PROPERTY | 2003-10-09 15:30 | 2003-10-09 16:00 | 10 | 10 | LINE BREAK | 034007 | FAX 858-571-6972 | 10//17/03 10:25 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-10-09 15:30 | 2003-10-09 16:00 | 1 | 10 | 10 | 0 | 34082 Capistrano by the Sea | Dana Point | 92629 | OC | LATERAL LINE | 0 | NONE | LINE BREAK | Private lateral separated (broke) approx. 20' upstream from SCWD sewer main | SCWD laid sandbags at curb to contain spill (leak) and excavated lateral for homeowner and vacuumed up sewage. Homeowner reconnected lateral and backfilled hole. | N | N | N | n/a | n/a | Sewage was contained at location of spill/leak and soaked into ground and was recovered with vactor | Y | N | N | n/a | 0 | Private Service Lateral
|  | South Coast County Water District | South Coast County Water District | 2003-10-17 09:00 | 2003-10-17 09:10 | 10 | 10 | LINE BREAK | 034008 | FAX 858-571-6972 | 2003-10-17 16:05 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-10-17 09:00 | 2003-10-17 09:10 | 1 | 10 | 10 | 0 | 31885 Circle Dirve | Laguna Beach | 92651 | OC | LIFT STATION | 0 | NONE | LINE BREAK | Sewage seeping from ground onto concrete/block steps approx 30-feet upstream of LS 7. Crews found a small pinhole leak had developed in the pipeline that runs from LS 7 to the main | LS 7 was turned off. Crews installed sandbags to contain the overflow and used a shop vac to recover the full amount. SCWD replaced the 4-inch line from LS 7 to the main line and rehabilitated LS | N | N | N | n/a | n/a | Sewage was contained and recovered at site of spill (leak) | Y | N | N | n/a | 0 | SCWD replaced 4" sewer line and rehabilitated LS 7 (this station services 3 homes)
|  | South Coast County Water District | PRIVATE PROPERTY | 2003-12-03 12:58 | 2003-12-03 13:15 | 10 | 0 | LINE BREAK | 034009 | FAX 858-571-6972 | 2003-12-05 12:00 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-12-03 12:58 | 2003-12-03 13:15 | 1 | 10 | 0 | 10 | 31501 Bluff Drive | Laguna Beach | 92651 | OC | LATERAL LINE | 0 | NONE | LINE BREAK | Land slide broke private sewer lateral causing it to separate | Crews removed dirt from slide and realigned and reconnected the sewer lateral | N | N | N | n/a | n/a | Leakage was contained at base of cliff and leaked into sand | Y | N | N | n/a | 0 | Private service lateral. Prior to repair SCWD contacted homeowner and informed him of situation. SCWD made interim repairs. Homeowner to have private plumber evaluate need for more permanent repair
|  | South Coast County Water District | PRIVATE PROPERTY | 2003-12-23 12:45 | 2003-12-23 13:10 | 10 | 10 | BLOCKAGE | 034010 | FAX 858-571-6972 | 2003-12-24 11:45 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-12-23 12:45 | 2003-12-23 13:10 | 1 | 10 | 10 | 0 | 26344 Via California | Capistrano Beach | 92624 | OC | LATERAL LINE | 0 | NONE | BLOCKAGE | Blockage was caused by heavy root buildup in the lateral | Crews cut the bad section of sewer lateral out, ran root cutter in lateral to remove roots and installed new section of pipe | N | N | N | n/a | n/a | District crews used sand bags at the curb to contain the overflow | Y | N | N | n/a | 0 | Private service lateral
|  | South Coast County Water District | South Coast County Water District | 2003-12-27 22:22 | 2004-01-01 11:45 | 21000 | 750 | OTHER | 034011 | FAX 858-571-6972 | 2004-01-01 17:00 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-12-27 22:22 | 2004-01-01 11:45 | 20 | 21000 | 750 | 20250 | 33801 Niguel Shores Drive | Dana Point | 92629 | OC | FORCE MAIN | 0 | NONE | OTHER | 1-1/2" Hole in forcemain approx. 1100' upstream of Lift Station 5 | SCWD Crews excavated the forcemain. A steel repair clamp was used to seal the leak as a temporary repair on 1/1/04. SCWD crews and contractor reexcavated the line on 1/6/04 and removed an 18' section of ductile iron pipe and replaced section with C-900 | N | Y | Y | PACFIC OCEAN | na | PACIFIC OCEAN | Y | N | Y | Dana Strands Beach from the northern point to 1000 feet downcoast of the Selva Ramp | 4 | District is reporting date of overflow start as 12/27/03 because the District Water Dept was notified of a water line leak on that date. Crew determined that the cause was a reclaimed water line in the same area. It was later determined that this diagno
|  | Trabuco Canyon Water District | Trabuco Canyon Water District | 2003-08-09 06:45 | 2003-08-09 06:46 | 5 | 5 | PUMP STATION FAILURE | 038007 |  | 2003-08-09 08:30 | Kris Hanberg | 949-858-0277 | Trabuco Canyon Water District | Trabuco Canyon Water District | 2003-08-09 06:45 | 2003-08-09 06:46 | 0.2 | 5 | 5 | 0 | 21379 Heritage Street | Trabuco Canyon | 92679 | OC | Herutage Lift Station | 0 |  | PUMP STATION FAILURE | Bubbler compressor failure | replaced compressor | N | N | N | none | none | stayed on site | Y | Y | N
|  | Santa Margarita Water District | Santa Margarita Water District | 1989-01-01 | 2003-07-08 11:30 | 0 | 0 | OTHER | 034001 | Fax (858) 467-2952 | 2003-07-08 12:30 | Steve Francis | (949) 459-4539 | Santa Margarita Water District | Santa Margarita Water District | 1989-01-01 | 2003-07-08 11:30 | 0 | 0 | 0 | 0 | 26626 Domingo | Mission Viejo | 92688 | OC | Sewer Lateral | 0 | 0 | OTHER | Sewer lateral connection was not connected at the main. | Installed new pipe and connected it to main. Removed contaminated soil. | N | N | N | None | None | Subsuface perculation into surrounding soil. | Y | N | N |  |  | Occupancy for residence was released in 1989. It could not be determined how much sewage passed through the pipe to the main or how much perculated into the soil.
|  | Santa Margarita Water District | Santa Margarita Water District | 2003-08-16 12:50 | 2003-08-16 13:02 | 2880 | 400 | OTHER | 034002 | Fax (858) 467-2952 | 2003-08-16 14:15 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2003-08-16 12:50 | 2003-08-16 13:02 | 240 | 2880 | 400 | 2480 | Alicia/Santa Margarita Pkwy | Rncho Snta Margarita | 92688 | OC | Trabuco Lift Station | 0 | 0 | OTHER | Power failure at lift station. Generator started and ran for a short while until a circuit board in the generator shorted out and shut down the power. The generator is tested under load on a regular basis. | Crew sand-bagged the storm drain to capture some flow and were able to restart the generator. Repair personnel replaced faulty components. | N | Y | Y | Trabuco Creek | San Juan Creek | 400 gallons Vactor truck and 2,480 gallons San Juan Creek | Y | Y | N |  |  | Sand berm was in place at mouth of San Juan Creek.
|  | Santa Margarita Water District | Santa Margarita Water District | 2003-12-10 09:30 | 2003-12-12 14:20 | 40 | 700 | OTHER | 034003 | Quarterly Report | Quarterly Report | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2003-12-10 09:30 | 2003-12-12 14:20 | 0.1 | 40 | 700 | 0 | San Blas | Mission Viejo | 92690 | OC | Tres Vistas Pump Station Force Main | 0 | 0 | OTHER | Street light pedestal settled on top of four-inch force main causing a hairline crack. Leak was very slight, and only during pump operation. | Crews removed the pedestal and replaced the section of pipe. All contaminated soil was removed. | N | N | N | None | None | Vactor Truck | Y | N | N |  |  | The 700 gallons recovered included wash water.
|  | Santa Margarita Water District | Santa Margarita Water District | 2003-12-26 10:40 | 2003-12-26 11:50 | 140 | 20 | ROOTS | 034004 | Fax (858) 467-2952 | 2003-12-26 12:00 | Steve Francis | (949) 459-6539 | Santa Margarita Water District | Santa Margarita Water District | 2003-12-26 10:40 | 2003-12-26 11:50 | 2 | 140 | 20 | 120 | Vista Del Verde & San Miguel | Coto de Caza | 92688 | OC | Sewer Manhole | 0 | 0 | ROOTS | Root intrusion caused sewage to backup into stream manhole. | Removed roots from sewer line, scheduled video to assess treatment or repairs. | Y | Y | Y | Coto Creek | Dana Point | Recovered 20 gallons with the Vactor from the catch basin. | Y | N | N
|  | County of San Diego | County of San Diego | 2003-08-30 15:00 | 2003-08-30 16:20 | 2800 | 1800 | ROOTS | 034001 | VOICE MAIL 571-6922 | 9/01/03 1000 | Bob Braun | 619-660-2007 | Co.SD | Co.SD | 8-30-03 1500 | 8-30-03 1620 | 8 | 2800 | 1800 | 1000 | 13881 Hwy 8 | Lakeside |  | SD | 398-30-341B | 0 | NA | Roots | Roots mass in manhole | Removed roots, rodded line | n | n | n | na | na | Private property, field | y | y | n | ma | 0 | Physically inspecting all manholes associated with this large high capacity line for similar problems
|  | Eastern Municipal Water District | Murrieta County Water District | 2003-10-16 | 2003-10-16 | 100 | 0 | CONSTRUCTION | 010208 | Quarterly Report | 2003-10-16 | Anne Briggs | 909-928-3777 | Eastern Municipal Water District | Murrieta County Water District | 2003-10-16 | 2003-10-16 |  | 100 | 0 | 100 | Washington / Santa Fe | Murrieta | 92562 | RV | Manhole | 0 | 0 | CONSTRUCTION | Construction asphalt in line from new development | Contractor hired by MCWD to clean out the line | N | N | N | n/a | n/a | Ground | Y | Y | N | n/a | 0
|  | Eastern Municipal Water District | Eastern Municipal Water District | 2003-10-20 | 2003-10-20 | 30 | 30 | CONSTRUCTION | 010209 | Quarterly Report | 2003-10-20 | Roger Turner | 909-928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 2003-10-20 | 2003-10-20 |  | 30 | 30 | 0 | Kentfield Dr/Triburon | Temecula | 92592 | RV | Manhole | 0 | 0 | CONSTRUCTION | 8 inch plug left in line | Removed plug from line | N | N | N | n/a | n/a | n/a | Y | N | N | n/a | 0
|  | Eastern Municipal Water District | Eastern Municipal Water District | 2003-11-03 09:00 | 2003-11-03 10:00 | 7000 | 7000 | CONSTRUCTION | 010210 | Brian Kelly | 2003-11-03 10:00 | Anne Briggs | 909-928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 2003-11-03 09:00 | 2003-11-03 10:00 |  | 7000 | 7000 | 0 | Crown Hill/Paraquay | Temecula | 92592 | RV | Manhole | 0 | 0 | CONSTRUCTION | Rope left in line | Sending Administrative Order to Developer | N | N | N | n/a | n/a | New storm water retention pond | Y | Y | Y | At retention pond | 7

## Drop-down lists
Sewer Agency List | County | SSO Cause Short | Yes or No
Buena Sanitary District | OC | BLOCKAGE | Y
Carlsbad Municipal Water District | RV | CONSTRUCTION | N
City of Chula Vista | SD | DEBRIS
City of Coronado |  | FLOOD DAMAGE
City of Del Mar |  | GREASE
City of El Cajon |  | INFILTRATION
City of Encinitas |  | LINE BREAK
City of Escondido |  | MANHOLE FAILURE
City of Imperial Beach |  | OTHER
City of La Mesa |  | POWER FAILURE
City of Laguna Beach |  | PRIVATE PROPERTY
City of Lemon Grove |  | PUMP STATION FAILURE
City of National City |  | ROCKS
City of Oceanside |  | ROOTS
City of Poway |  | UNKNOWN
City of San Clemente |  | VANDALISM
City of San Diego
City of San Juan Capistrano
City of Solana Beach
City of Vista
County of San Diego
Eastern Municipal Water District
Elsinore Valley Municipal Water District
El Toro Water District
Emerald Bay Community Services District
Fairbanks Ranch Community Services District
Fallbrook Public Utilities District
Irvine Ranch Water District
Leucadia County Water District
Moulton Niguel Water District
Murrieta County Water District
Olivenhain Municipal Water District
Otay Water District
Padre Dam Municipal Water District
Pauma Valley Community Services District
Rainbow Municipal Water District
Ramona Municipal Water District
Rancho Santa Fe Community Services District
Rancho California Water District
Santa Margarita Water District
South Coast County Water District
Trabuco Canyon Water District
U.S. Marine Corps, Camp Pendleton
U.S. Navy Public Works Center
Vallecitos Water District
Valley Center Municipal Water District
Whispering Palms Community Services District
Private Party