## Slide 1: Surfwood Mutual Water Corporation CA2300590 Mendocino County Jar Test
by Guy Schott, P.E
March 2, 2023

## Slide 2: Source Water: Jack Peter’s Creek Roughing Filter followed by Multi-Media Filtration
Source Water Characteristics
Turbidity: 6.8 NTU
pH: 7.10 – 7.17
UVT: 37.3%
UVA: 0.427/cm
0.4 um Filtered
Turbidity: 0.97 NTU
UVT: 41.9%
UVA: 0.377/cm

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Applied Coagulants for Jar Testing (1)
Pro Pac 926 (NTU Technologies)
35% Aluminum Chlorohydrate
35% Water
23.62% Al2O3
30% pDADMAC solution
83% Basicity
SG = 1.25-1.34
NSF limit: 83 mg/L as Product
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate
35-45% Water
~18.9% Al2O3
~10.5% Al
83% Basicity
20% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 50 mg/L as Product;
Product dose 10 mg/L = 1 mg/L polyamines active

## Slide 5: Applied Coagulants for Jar Testing (2)
960 (NTU Technologies)
33% Polyaluminum Hydroxychlorosulfate
67% Water
SG = 1.29
NSF limit: 250 mg/L as Product
BWS, Inc.
Greg Nieckarz, Ph.D.
Greg.niekarz@bws.works
541-953-5112
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 250 mg/L as Product

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.10-7.17
LCA #1:
CTC-00011: 118 mg/L as product (no pH adjustment)
Final pH: 7:09
LCA #2:
960: 90 mg/L as product (no pH adjustment)
Final pH: 6.30
LCA #3:
9890: 36 mg/L as product (no pH adjustment)
Final pH: 6.91

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Filtrate and %UVT/UVA Analysis
For this study, all jars were samples for Filtrate and %UVT/UVA analysis immediately at the end of the flocculation period.

## Slide 9: Surfwood MWC; Jar Test 1 - 4 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9890 (ACH/PY) mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 25 | 3.86 | 61.0 | 0.214 | 43.2 | 10.8
J2 | 30 | 0.26 | 85.8 | 0.066 | 71.9 | 5.22
J3 | 35 | 0.18 | 85.3 | 0.068 | 71.4 | 8.16
J4 | 40 | 0.17 | 86.5 | 0.062 | 72.9 | 3.35

## Slide 10: Surfwood MWC; Jar Test 5 - 12 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | CTC-00011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J5 | 50 | 5.83 | 42.5 | 0.370 | 1.9 | 10.2
J6 | 55 | 8.06 | 42.4 | 0.371 | 1.6 | 13.6
J7 | 60 | 9.30 | 43.0 | 0.365 | 3.2 | 14.7
J8 | 65 | 6.58 | 52.5 | 0.279 | 26.0 | 14.9
J9 | 100 | 0.12 | 81.8 | 0.086 | 77.2 | 20.2
J10 | 110 | 0.37 | 83.0 | 0.080 | 78.8 | 29.7
J11 | 120 | 0.28 | 85.8 | 0.066 | 82.5 | 37.3
J12 | 130 | 0.25 | 87.5 | 0.057 | 84.9 | 46.0

## Slide 11: Surfwood MWC; Jar Test 13 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 926 (ACH/pDADMAC) mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J13 | 30 | 4.45 | 40.7 | 0.389 | 0 | 7.88
J14 | 35 | 4.44 | 40.6 | 0.390 | 0 | 8.07
J15 | 40 | 4.41 | 42.9 | 0.366 | 2.9 | 8.16
J16 | 45 | 4.60 | 39.1 | 0.407 | 0 | -

## Slide 12: Surfwood MWC; Jar Test 17 - 23 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 960 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 70 | 3.78 | 69.2 | 0.159 | 57.8 | 11.1
J18 | 80 | 0.35 | 89.3 | 0.049 | 87.0 | 6.2
J19 | 90 | 0.10 | 92.7 | 0.032 | 91.5 | 2.54
J20 | 100 | 0.07 | 94.0 | 0.026 | 93.1 | 2.09
J21 | 100 | 0.18 | 91.5 | 0.038 | 88.7 | 1.98
J22 | 110 | 0.07 | 94.3 | 0.025 | 93.4 | 2.48
J23 | 120 | 0.13 | 94.4 | 0.024 | 93.6 | 3.11

## Slide 13: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 9890

## Slide 14: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
25 mg/L 9890
Filtrate 3.86 NTU
UVT: 61.0%
UVA: 0.214/cm
UVA Reduction: 43.2%
Settled: 10.8 NTU
30 mg/L 9890
Filtrate 0.26NTU
UVT: 85.8%
UVA: 0.066/cm
UVA Reduction: 71.9%
Settled: 5.22 NTU
35 mg/L 9890
Filtrate 0.18 NTU
UVT: 85.3%
UVA: 0.068/cm
UVA Reduction: 71.4%
Settled: 8.16 NTU
40 mg/L 9890
Filtrate 0.17 NTU
UVT: 86.5%
UVA: 0.062/cm
UVA Reduction: 72.9%
Settled: 3.35 NTU

## Slide 15: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.

## Slide 16: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant CTC-00011

## Slide 17: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
50 mg/L CTC-00011
Filtrate 5.83 NTU
UVT: 42.5%
UVA: 0.378/cm
UVA Reduction: 1.9%
Settled: 10.2 NTU
55 mg/L CTC-00011
Filtrate 8.06 NTU
UVT: 42.4%
UVA: 0.371/cm
UVA Reduction: 1.6%
Settled: 13.6 NTU
60 mg/L CTC-00011
Filtrate 9.30 NTU
UVT: 43.0%
UVA: 0.365/cm
UVA Reduction: 3.2%
Settled: 14.7 NTU
65 mg/L CTC-00011
Filtrate 6.58 NTU
UVT: 52.5%
UVA: 0.279/cm
UVA Reduction: 26.0%
Settled: 14.9 NTU

## Slide 18: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.

## Slide 19: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant CTC-00011

## Slide 20: Jars 9-12: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
100 mg/L CTC-00011
Filtrate 0.12 NTU
UVT: 81.8%
UVA: 0.086/cm
UVA Reduction: 77.2%
Settled: 20.2 NTU
110 mg/L CTC-00011
Filtrate 0.37 NTU
UVT: 83.0%
UVA: 0.080/cm
UVA Reduction: 78.8%
Settled: 29.7 NTU
120 mg/L CTC-00011
Filtrate 0.28 NTU
UVT: 85.8%
UVA: 0.066/cm
UVA Reduction: 82.5%
Settled: 37.3 NTU
130 mg/L CTC-00011
Filtrate 0.25 NTU
UVT: 87.5%
UVA: 0.057/cm
UVA Reduction: 84.9%
Settled: 46.0 NTU

## Slide 21: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.

## Slide 22: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 960

## Slide 23: Jars 13-16: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
70 mg/L 960
Filtrate 2.78 NTU
UVT: 69.2%
UVA: 0.159/cm
UVA Reduction: 57.8%
Settled: 11.1 NTU
80 mg/L 960
Filtrate 0.35 NTU
UVT: 89.3%
UVA: 0.049/cm
UVA Reduction: 87.0%
Settled: 6.2 NTU
90 mg/L 960
Filtrate 0.10 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 91.5%
Settled: 2.54 NTU
100 mg/L 960
Filtrate 0.07 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 93.1%
Settled: 2.09 NTU

## Slide 24: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.

## Slide 25: Jars 17-19 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 960

## Slide 26: Jars 17-19: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
100 mg/L 960
Filtrate 0.18 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 88.7%
Settled: 1.98 NTU
110 mg/L 960
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 93.4%
Settled: 2.48 NTU
120 mg/L 960
Filtrate 0.13 NTU
UVT: 94.4%
UVA: 0.025/cm
UVA Reduction: 93.6%
Settled: 3.11 NTU

## Slide 27: Jars 17-19: After 25-minutes of settling, settled water turbidity is taken.

## Slide 28: Jars 20-23 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 926

## Slide 29: Jars 20-23: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
30 mg/L 926
Filtrate 4.45 NTU
UVT: 40.7%
UVA: 0.389/cm
UVA Reduction: 0%
Settled: 7.88 NTU
35 mg/L 926
Filtrate 4.44 NTU
UVT: 40.6%
UVA: 0.390/cm
UVA Reduction: 0%
Settled: 8.07 NTU
40 mg/L 926
Filtrate 4.41 NTU
UVT: 42.9%
UVA: 0.366/cm
UVA Reduction: 0%
Settled: 8.16 NTU
45 mg/L 926
Filtrate 4.60 NTU
UVT: 39.1%
UVA: 0.407/cm
UVA Reduction: 0%
Settled: - NTU

## Slide 30: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 20-30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate). For this study, sample was taken immediately at the end of flocculation process.
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 31: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 32: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 33: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 34: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 35: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Jar Test Results/Procedures for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right video training https://youtu.be/aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732