## Slide 1: Heritage Ranch CSD CA4010012 San Luis Obispo County Jar Test
by Guy Schott, P.E.
February 22, 2021

## Slide 2: Source Water: Well 01 (Nacimiento River)

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Heritage Ranch CSD Source Water Characteristics, February 22, 2021
Source
pH: 7.82
Alkalinity: 70 mg/L as CaCO3
Turbidity: 88 NTU
UVT: 30.9%,
UVA: 0.508/cm
0.4 um Filtered
Turbidity: 0.86 NTU
UVT: 63.1%,
UVA: 0.199/cm
Source (post-KMnO4/PAC)
pH: 7.88
Alkalinity: 73 mg/L as CaCO3
Turbidity: 65 NTU
UVT: 41.3%,
UVA: 0.384/cm
0.4 um Filtered
Turbidity: 0.61 NTU
UVT: 68.0%,
UVA: 0.167/cm

## Slide 5: Heritage Ranch CSD WTP Water Characteristics, February 22, 2021 Treatment Plant: Plate Settlers followed by Roberts Filtration
Plant Coagulant Dose:
Alum(dry): 34.5 mg/L
Clarifloc C-378: 7 mg/L (pDADMAC solution)
Plant Filtrate Water (pre-chlorination
pH: 7.42
Alkalinity: 60 mg/L as CaCO3
Turbidity: 0.19 NTU
UVT: 86.5%,
UVA: 0.062/cm
Filtrate Water (post-chlorine)
Turbidity: 0.11 NTU
UVT: 90.9%,
UVA: 0.041/cm

## Slide 6: Applied Coagulants for Jar Testing (1)
Aluminum Sulfate (Product)
Al2(SO4)3*14.3H20 (Liquid)
48% Aluminum Sulfate
52% Water
8.2% Al2O3
4.3% Al
0% Basicity
SG = 1.32
NSF limit: 400 mg/L (product)
As hydrated Al2(SO4)3*14.3H20
17% Al2O3
Polydyne Incorporated
Clarifloc C-378
SG = 1.0 – 1.2
pDADMAC (20% active, 80% H2O)
NSF limit: 50 mg/L (product)
Product dose 5 mg/L = 1 mg/L pDADMAC active

## Slide 7: Applied Coagulants for Jar Testing (2)
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 40 mg/L = 1 mg/L polyamines active
BWS, Inc.
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 250 mg/L as Product

## Slide 8: Applied Coagulants for Jar Testing (3)
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product;

## Slide 9: Polyamine C59H108N14O10 MW: 1,173.6 g/mol

## Slide 10: Diallyldimethylammonium chloride or N-allyl-N,N-dimethylprop-2-en-1-aminium chloride pDADMAC C8H16ClN MW: 161.67 g/mol
N
+
CH3
CH3
CH2
CH
CH2
CH2
CH
CH2
Cl-

## Slide 11: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.8 (post KMnO4 oxidation)
LCA #1: Alum: 45.8 mg/L as hydrated
pH adjusted to 6.7 with acetic acid
LCA #2: 9810: 40 mg/L
pH adjusted to 7.6 with acetic acid
LCA #3: AdvFloc CTC-00011: 136 mg/L
pH adjusted to 7.6 with acetic acid

## Slide 12: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 13: Heritage Ranch CSD; Source Well 01 (Nacimiento River) Summary of Plant Coagulant/Dose Jar vs. Optimum Dose and Coagulants
Jar# | Alum mg/L | AdvFloc CTC-0011 mg/L | 9800 mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
A | 35 | 0 | 0 | 6.0 | 0.10 | 87.0 | 0.061 | 69.3 | 3.22
vs. |  |  |  |  |  |  |  |  | 
B | 70 | 0 | 0 | 6.0 | 0.05 | 90.7 | 0.042 | 78.9 | 3.45
C | 0 | 160 | 0 | 6.0 | 0.05 | 92.0 | 0.036 | 81.9 | 1.16
D | 0 | 0 | 70 | 6.0 | 0.05 | 91.3 | 0.039 | 80.4 | 2.84

## Slide 14: Jar Test – Filtrate Water Spiked with 2.2 mg/L NaOCl Plant Coagulant Dose vs. Optimum Dose and Coagulant
Chart: Chlorine Residual Over Time
| 0 | 8.1999999999999993 | 20.299999999999997 | 32.199999999999996 | 44.5 | 56.8 | 68.8 | 92 | 116
Alum: 35 mg/L, CatFloc C-378: 6.0 mg/L, UVA: 0.061/cm | 0.78 | 0.43 | 0.22 | 0.17 | 0.1 | 0.08 | 0.07 | 0.06 | 0.04
Alum: 70 mg/L, CatFloc C-378: 6.0 mg/L, UVA: 0.042/cm | 0.82 | 0.65 | 0.49 | 0.37 | 0.3 | 0.25 | 0.2 | 0.13 | 0.07
AdvFloc: 160 mg/L, CatFloc C-378: 6.0 mg/L, UVA: 0.036/cm | 1 | 0.67 | 0.53 | 0.42 | 0.35 | 0.27 | 0.23 | 0.15 | 0.13

## Slide 15: Source Water: (pH: 7.88, Alkalinity: 73 mg/L)
Coagulant | Chemical Dose, mg/L | Alkalinity Consumed mg/L as CaCO3 | Treated Water Alkalinity mg/L as CaCO3 | *Treated Water pH
Alum (dry) | 35 | 17.5 | 55.5 | 6.81
Alum (dry) | 70 | 35.1 | 37.9 | 6.36
AdvFloc | 160 | 20.8 | 52.2 | 6.71
9810 | 65 | 7.3 | 65.7 | 7.20
9800 | 70 | 8.3 | 64.7 | 7.15
*Note: Predicted treated water pH is based on a closed system (no CO2 loss). In an open system (water exposed to atmosphere), lost of CO2 can be up to 60% thereby raising pH. Alkalinity is not affected by CO2 lost. The Heritage Ranch CSD treatment plant is considered an open system.

## Slide 16: Heritage Ranch CSD; Source Well 01; Jar Test 1 - 8 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 35 | 1.06 | 82.3 | 0.084 | 57.8 | 13.3
J2 | 40 | 1.00 | 82.5 | 0.083 | 58.3 | 11.4
J3 | 45 | 0.66 | 84.1 | 0.075 | 62.3 | 8.68
J4 | 50 | 0.28 | 87.1 | 0.059 | 70.4 | 3.79
J5 | 55 | 0.27 | 87.4 | 0.058 | 70.9 | 5.03
J6 | 60 | 0.26 | 88.3 | 0.053 | 73.4 | 4.29
J7 | 65 | 0.26 | 88.5 | 0.052 | 73.9 | 3.79
J8 | 70 | 0.16 | 89.8 | 0.046 | 76.9 | 2.79

## Slide 17: Heritage Ranch CSD; Source Well 01; Jar Test 9 - 16 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | AdvFloc CTC-0011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 130 | 0.09 | 90.3 | 0.044 | 77.9 | 0.71
J10 | 140 | 0.12 | 90.3 | 0.043 | 78.4 | 0.90
J11 | 150 | 0.09 | 91.0 | 0.040 | 79.9 | 0.73
J12 | 160 | 0.07 | 91.1 | 0.040 | 79.9 | 0.42
J13 | 170 | 0.08 | 91.6 | 0.037 | 81.4 | 0.53
J14 | 180 | 0.09 | 91.8 | 0.037 | 81.4 | 0.64
J15 | 190 | 0.07 | 91.6 | 0.037 | 81.4 | 0.61
J16 | 200 | 0.06 | 92.1 | 0.035 | 82.4 | 0.43

## Slide 18: Heritage Ranch CSD; Source Well 01; Jar Test 17 - 24 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 35 | 0.25 | 87.1 | 0.059 | 70.4 | 4.08
J18 | 40 | 0.29 | 88.1 | 0.054 | 72.9 | 3.31
J19 | 45 | 0.28 | 89.9 | 0.046 | 76.9 | 3.18
J20 | 50 | 0.22 | 89.4 | 0.048 | 75.9 | 3.41
J21 | 55 | 0.26 | 89.5 | 0.048 | 75.9 | 3.18
J22 | 60 | 0.25 | 89.8 | 0.046 | 76.9 | 3.10
J23 | 65 | 0.06 | 90.8 | 0.041 | 79.4 | 3.38
J24 | 70 | 0.18 | 90.6 | 0.042 | 78.9 | 2.93

## Slide 19: Heritage Ranch CSD; Source Well 01; Jar Test 25 - 28 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 35 | 0 | 0.72 | 83.8 | 0.076 | 61.8 | 10.2
J26 | 35 | 2.0 | 0.12 | 85.7 | 0.066 | 66.8 | 4.93
J27 | 35 | 4.0 | 0.17 | 86.4 | 0.063 | 68.3 | 2.90
J28 | 35 | 6.0 | 0.10 | 87.5 | 0.057 | 71.4 | 3.74

## Slide 20: Heritage Ranch CSD; Source Well 01; Jar Test 29 - 36 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J29 | 35 | 6.0 | 0.08 | 87.9 | 0.056 | 71.9 | 3.15
J30 | 45 | 6.0 | 0.05 | 89.2 | 0.049 | 75.4 | 2.68
J31 | 50 | 6.0 | 0.05 | 89.8 | 0.046 | 76.9 | 2.84
J32 | 55 | 6.0 | 0.04 | 90.3 | 0.044 | 77.9 | 3.86
J33 | 35 | 6.0 | 0.11 | 87.5 | 0.057 | 71.4 | 3.38
J34 | 60 | 6.0 | 0.04 | 90.3 | 0.044 | 77.9 | 4.79
J35 | 65 | 6.0 | 0.05 | 90.9 | 0.041 | 79.4 | 3.64
J36 | 70 | 6.0 | 0.04 | 91.1 | 0.040 | 79.9 | 3.95

## Slide 21: Heritage Ranch CSD; Source Well 01; Jar Test 37 - 40 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | AdvFloc CTC-0011 mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J37 | 160 | 0 | 0.08 | 91.4 | 0.038 | 80.9 | 0.38
J38 | 160 | 6.0 | 0.06 | 92.3 | 0.034 | 82.9 | 1.0
J39 | 180 | 0 | 0.08 | 91.9 | 0.036 | 81.9 | 0.67
J40 | 180 | 6.0 | 0.05 | 92.6 | 0.033 | 83.4 | 0.86

## Slide 22: Heritage Ranch CSD; Source Well 01; Jar Test 41 - 48 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 9800 mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J41 | 45 | 6.0 | 0.10 | 90.2 | 0.044 | 77.9 | 2.21
J42 | 50 | 6.0 | 0.07 | 90.7 | 0.042 | 78.9 | 2.57
J43 | 55 | 6.0 | 0.06 | 91.3 | 0.039 | 80.4 | 2.84
J44 | 60 | 6.0 | 0.07 | 91.4 | 0.038 | 80.9 | 2.67
J45 | 65 | 6.0 | 0.10 | 90.9 | 0.041 | 79.4 | 2.48
J46 | 70 | 6.0 | 0.08 | 91.5 | 0.038 | 80.9 | 2.54
J47 | 75 | 6.0 | 0.07 | 91.6 | 0.037 | 81.4 | 2.65
J48 | 80 | 6.0 | 0.08 | 91.6 | 0.037 | 81.4 | 2.07

## Slide 23: Heritage Ranch CSD; Source Well 01; Jar Test 49 - 52 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min) Results compares plant dose (Jar 49) with optimum Alum dose and other coagulants (AdvFloc & 9800).
Jar # | Alum mg/L | AdvFloc CTC-0011 mg/L | 9800 mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J49 | 35 | 0 | 0 | 6.0 | 0.10 | 87.0 | 0.060 | 69.8 | 3.22
J50 | 70 | 0 | 0 | 6.0 | 0.05 | 90.7 | 0.042 | 78.9 | 3.45
J51 | 0 | 160 | 0 | 6.0 | 0.05 | 92.0 | 0.036 | 81.9 | 1.16
J52 | 0 | 0 | 70 | 6.0 | 0.05 | 91.3 | 0.039 | 80.4 | 2.84

## Slide 24: Heritage Ranch CSD; Source Well 01; Jar Test 53 - 56 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min) Jars 53 & 55 (Source, without pre-oxidation); Jars 54 & 56 (Source, post-oxidation KMnO4)
Jar # | Alum mg/L | AdvFloc CTC-0011 mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J53 | 70 | 0 | 6.0 | 0.08 | 89.2 | 0.049 | 75.4 | 6.45
J54 | 70 | 0 | 6.0 | 0.05 | 90.8 | 0.042 | 78.9 | 3.14
J55 | 0 | 160 | 6.0 | 0.10 | 90.8 | 0.041 | 79.4 | 3.69
J56 | 0 | 160 | 6.0 | 0.05 | 92.1 | 0.035 | 82.4 | 0.93

## Slide 25: Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulant Alum

## Slide 26: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
35 mg/L Alum
Filtrate 1.06 NTU
UVT: 82.3%
UVA: 0.084/cm
UVA Reduction 57.8%
Settled: 13.3 NTU
40 mg/L Alum
Filtrate 1.00 NTU
UVT: 82.5%
UVA: 0.083/cm
UVA Reduction 58.3%
Settled: 11.4 NTU
45 mg/L Alum
Filtrate 0.66 NTU
UVT: 84.1%
UVA: 0.075/cm
UVA Reduction 62.3%
Settled: 8.68 NTU
50 mg/L Alum
Filtrate 0.28 NTU
UVT: 87.1%
UVA: 0.059/cm
UVA Reduction 70.4%
Settled: 3.79 NTU

## Slide 27: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 28: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L Alum
Filtrate 1.06 NTU
UVT: 82.3%
UVA: 0.084/cm
UVA Reduction 57.8%
Settled: 13.3 NTU
40 mg/L Alum
Filtrate 1.00 NTU
UVT: 82.5%
UVA: 0.083/cm
UVA Reduction 58.3%
Settled: 11.4 NTU
45 mg/L Alum
Filtrate 0.66 NTU
UVT: 84.1%
UVA: 0.075/cm
UVA Reduction 62.3%
Settled: 8.68 NTU
50 mg/L Alum
Filtrate 0.28 NTU
UVT: 87.1%
UVA: 0.059/cm
UVA Reduction 70.4%
Settled: 3.79 NTU

## Slide 29: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulant Alum

## Slide 30: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
55 mg/L Alum
Filtrate 0.27 NTU
UVT: 87.4%
UVA: 0.058/cm
UVA Reduction 70.9%
Settled: 5.03 NTU
60 mg/L Alum
Filtrate 0.26 NTU
UVT: 88.3%
UVA: 0.053/cm
UVA Reduction 73.4%
Settled: 4.29 NTU
65 mg/L Alum
Filtrate 0.26 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction 73.9%
Settled: 3.79 NTU
70 mg/L Alum
Filtrate 0.16 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 76.9%
Settled: 2.79 NTU

## Slide 31: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 32: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
55 mg/L Alum
Filtrate 0.27 NTU
UVT: 87.4%
UVA: 0.058/cm
UVA Reduction 70.9%
Settled: 5.03 NTU
60 mg/L Alum
Filtrate 0.26 NTU
UVT: 88.3%
UVA: 0.053/cm
UVA Reduction 73.4%
Settled: 4.29 NTU
65 mg/L Alum
Filtrate 0.26 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction 73.9%
Settled: 3.79 NTU
70 mg/L Alum
Filtrate 0.16 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 76.9%
Settled: 2.79 NTU

## Slide 33: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulant AdvFloc CTC-00011

## Slide 34: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
130 mg/L AdvFloc
Filtrate 0.09 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 77.9%
Settled: 0.71 NTU
140 mg/L AdvFloc
Filtrate 0.12 NTU
UVT: 90.3%
UVA: 0.043/cm
UVA Reduction 78.4%
Settled: 0.90 NTU
150 mg/L AdvFloc
Filtrate 0.09 NTU
UVT: 90.3%
UVA: 0.040/cm
UVA Reduction 79.9%
Settled: 0.73 NTU
160 mg/L AdvFloc
Filtrate 0.07 NTU
UVT: 90.3%
UVA: 0.040/cm
UVA Reduction 79.9%
Settled: 0.42 NTU

## Slide 35: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 36: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
130 mg/L AdvFloc
Filtrate 0.09 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 77.9%
Settled: 0.71 NTU
140 mg/L AdvFloc
Filtrate 0.12 NTU
UVT: 90.3%
UVA: 0.043/cm
UVA Reduction 78.4%
Settled: 0.90 NTU
150 mg/L AdvFloc
Filtrate 0.09 NTU
UVT: 90.3%
UVA: 0.040/cm
UVA Reduction 79.9%
Settled: 0.73 NTU
160 mg/L AdvFloc
Filtrate 0.07 NTU
UVT: 90.3%
UVA: 0.040/cm
UVA Reduction 79.9%
Settled: 0.42 NTU

## Slide 37: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulant AdvFloc CTC-00011

## Slide 38: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
170 mg/L AdvFloc
Filtrate 0.08 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 0.53 NTU
180 mg/L AdvFloc
Filtrate 0.09 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 0.64 NTU
190 mg/L AdvFloc
Filtrate 0.07 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 0.61 NTU
200 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 82.4%
Settled: 0.43 NTU

## Slide 39: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 40: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
170 mg/L AdvFloc
Filtrate 0.08 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 0.53 NTU
180 mg/L AdvFloc
Filtrate 0.09 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 0.64 NTU
190 mg/L AdvFloc
Filtrate 0.07 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 0.61 NTU
200 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 82.4%
Settled: 0.43 NTU

## Slide 41: Jars 17-20 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulant 9810

## Slide 42: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
35 mg/L 9810
Filtrate 0.25 NTU
UVT: 87.1%
UVA: 0.059/cm
UVA Reduction 70.4%
Settled: 4.08 NTU
40 mg/L 9810
Filtrate 0.29 NTU
UVT: 88.1%
UVA: 0.054/cm
UVA Reduction 72.9%
Settled: 3.31 NTU
45 mg/L 9810
Filtrate 0.28 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 76.9%
Settled: 3.18 NTU
50 mg/L 9810
Filtrate 0.22 NTU
UVT: 89.4%
UVA: 0.048/cm
UVA Reduction 75.9%
Settled: 3.41 NTU

## Slide 43: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 44: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L 9810
Filtrate 0.25 NTU
UVT: 87.1%
UVA: 0.059/cm
UVA Reduction 70.4%
Settled: 4.08 NTU
40 mg/L 9810
Filtrate 0.29 NTU
UVT: 88.1%
UVA: 0.054/cm
UVA Reduction 72.9%
Settled: 3.31 NTU
45 mg/L 9810
Filtrate 0.28 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 76.9%
Settled: 3.18 NTU
50 mg/L 9810
Filtrate 0.22 NTU
UVT: 89.4%
UVA: 0.048/cm
UVA Reduction 75.9%
Settled: 3.41 NTU

## Slide 45: Jars 21-24 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulant 9810

## Slide 46: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
55 mg/L 9810
Filtrate 0.26 NTU
UVT: 89.5%
UVA: 0.048/cm
UVA Reduction 75.9%
Settled: 3.18 NTU
60 mg/L 9810
Filtrate 0.25 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 76.9%
Settled: 3.10 NTU
65 mg/L 9810
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 79.4%
Settled: 3.38 NTU
70 mg/L 9810
Filtrate 0.18 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 78.9%
Settled: 2.93 NTU

## Slide 47: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 48: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
55 mg/L 9810
Filtrate 0.26 NTU
UVT: 89.5%
UVA: 0.048/cm
UVA Reduction 75.9%
Settled: 3.18 NTU
60 mg/L 9810
Filtrate 0.25 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 76.9%
Settled: 3.10 NTU
65 mg/L 9810
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 79.4%
Settled: 3.38 NTU
70 mg/L 9810
Filtrate 0.18 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 78.9%
Settled: 2.93 NTU

## Slide 49: Jars 25-28 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulants Alum/CatFloc C-378

## Slide 50: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
35 mg/L Alum
0.0 mg/L C-378
Filtrate 0.72 NTU
UVT: 83.8%
UVA: 0.076/cm
UVA Reduction 61.8%
Settled: 10.2 NTU
35 mg/L Alum
2.0 mg/L C-378
Filtrate 0.12 NTU
UVT: 85.7%
UVA: 0.066/cm
UVA Reduction 66.8%
Settled: 4.93 NTU
35 mg/L Alum
4.0 mg/L C-378
Filtrate 0.17 NTU
UVT: 86.4%
UVA: 0.063/cm
UVA Reduction 68.3%
Settled: 2.90 NTU
35 mg/L Alum
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 87.5%
UVA: 0.057/cm
UVA Reduction 71.4%
Settled: 3.74 NTU

## Slide 51: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 52: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L Alum
0.0 mg/L C-378
Filtrate 0.72 NTU
UVT: 83.8%
UVA: 0.076/cm
UVA Reduction 61.8%
Settled: 10.2 NTU
35 mg/L Alum
2.0 mg/L C-378
Filtrate 0.12 NTU
UVT: 85.7%
UVA: 0.066/cm
UVA Reduction 66.8%
Settled: 4.93 NTU
35 mg/L Alum
4.0 mg/L C-378
Filtrate 0.17 NTU
UVT: 86.4%
UVA: 0.063/cm
UVA Reduction 68.3%
Settled: 2.90 NTU
35 mg/L Alum
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 87.5%
UVA: 0.057/cm
UVA Reduction 71.4%
Settled: 3.74 NTU

## Slide 53: Jars 29-32 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulants Alum/CatFloc C-378

## Slide 54: Jars 29-32: End of 5-minute flocculation (30 RPM) duration.
35 mg/L Alum
6.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 87.9%
UVA: 0.056/cm
UVA Reduction 71.9%
Settled: 3.15 NTU
45 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 75.4%
Settled: 2.68 NTU
50 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 76.9%
Settled: 2.84 NTU
55 mg/L Alum
6.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 77.9%
Settled: 3.86 NTU

## Slide 55: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 56: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L Alum
6.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 87.9%
UVA: 0.056/cm
UVA Reduction 71.9%
Settled: 3.15 NTU
45 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 75.4%
Settled: 2.68 NTU
50 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 76.9%
Settled: 2.84 NTU
55 mg/L Alum
6.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 77.9%
Settled: 3.86 NTU

## Slide 57: Jars 33-36 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulants Alum/CatFloc C-378

## Slide 58: Jars 33-36: End of 5-minute flocculation (30 RPM) duration.
35 mg/L Alum
6.0 mg/L C-378
Filtrate 0.11 NTU
UVT: 87.5%
UVA: 0.057/cm
UVA Reduction 71.4%
Settled: 3.38 NTU
60 mg/L Alum
6.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 77.9%
Settled: 4.79 NTU
65 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 79.4%
Settled: 3.64 NTU
70 mg/L Alum
6.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 79.9%
Settled: 3.95 NTU

## Slide 59: Jars 33-36: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 60: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L Alum
6.0 mg/L C-378
Filtrate 0.11 NTU
UVT: 87.5%
UVA: 0.057/cm
UVA Reduction 71.4%
Settled: 3.38 NTU
60 mg/L Alum
6.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 77.9%
Settled: 4.79 NTU
65 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 79.4%
Settled: 3.64 NTU
70 mg/L Alum
6.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 79.9%
Settled: 3.95 NTU

## Slide 61: Jars 37-40 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulants AdvFloc CTC-00011 /CatFloc C-378

## Slide 62: Jars 37-40: End of 5-minute flocculation (30 RPM) duration.
160 mg/L AdvFloc
0.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 80.9%
Settled: 0.38 NTU
160 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 82.9%
Settled: 1.0 NTU
180 mg/L AdvFloc
0.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 81.9%
Settled: 0.67 NTU
180 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 83.4%
Settled: 0.86 NTU

## Slide 63: Jars 37-40: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 64: Jars 37-40: After 25-minutes of settling, settled water turbidity is taken.
160 mg/L AdvFloc
0.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 80.9%
Settled: 0.38 NTU
160 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 82.9%
Settled: 1.0 NTU
180 mg/L AdvFloc
0.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 81.9%
Settled: 0.67 NTU
180 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 83.4%
Settled: 0.86 NTU

## Slide 65: Jars 41-44 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulants 9800/CatFloc C-378

## Slide 66: Jars 41-44: End of 5-minute flocculation (30 RPM) duration.
45 mg/L 9800
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 90.2%
UVA: 0.044/cm
UVA Reduction 77.9%
Settled: 2.21 NTU
50 mg/L 9800
6.0 mg/L C-378
Filtrate 0.07 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 78.9%
Settled: 2.57 NTU
55 mg/L 9800
6.0 mg/L C-378
Filtrate 0.06 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 80.4%
Settled: 2.84 NTU
60 mg/L 9800
6.0 mg/L C-378
Filtrate 0.07 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 80.9%
Settled: 2.67 NTU

## Slide 67: Jars 41-44: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 68: Jars 41-44: After 25-minutes of settling, settled water turbidity is taken.
45 mg/L 9800
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 90.2%
UVA: 0.044/cm
UVA Reduction 77.9%
Settled: 2.21 NTU
50 mg/L 9800
6.0 mg/L C-378
Filtrate 0.07 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 78.9%
Settled: 2.57 NTU
55 mg/L 9800
6.0 mg/L C-378
Filtrate 0.06 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 80.4%
Settled: 2.84 NTU
60 mg/L 9800
6.0 mg/L C-378
Filtrate 0.07 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 80.9%
Settled: 2.67 NTU

## Slide 69: Jars 45-48 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulants 9800/CatFloc C-378

## Slide 70: Jars 45-48: End of 5-minute flocculation (30 RPM) duration.
65 mg/L 9800
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 79.4%
Settled: 2.48 NTU
70 mg/L 9800
6.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 80.9%
Settled: 2.54 NTU
75 mg/L 9800
6.0 mg/L C-378
Filtrate 0.07 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 2.65 NTU
80 mg/L 9800
6.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 2.07 NTU

## Slide 71: Jars 45-48: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 72: Jars 45-48: After 25-minutes of settling, settled water turbidity is taken.
65 mg/L 9800
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 79.4%
Settled: 2.48 NTU
70 mg/L 9800
6.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 80.9%
Settled: 2.54 NTU
75 mg/L 9800
6.0 mg/L C-378
Filtrate 0.07 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 2.65 NTU
80 mg/L 9800
6.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 81.4%
Settled: 2.07 NTU

## Slide 73: Jars 49-52 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post-KMnO4 Oxidation Applied Coagulants Alum/AdvFloc CTC-00011 9800/CatFloc C-378

## Slide 74: Jars 49-52: End of 5-minute flocculation (30 RPM) duration.
35 mg/L Alum
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 87.0%
UVA: 0.060/cm
UVA Reduction 69.8%
Settled: 3.22 NTU
70 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 78.9%
Settled: 3.45 NTU
160 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.0%
UVA: 0.042/cm
UVA Reduction 81.9%
Settled: 1.16 NTU
70 mg/L 9800
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 80.4%
Settled: 2.84 NTU

## Slide 75: Jars 49-52: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 76: Jars 49-52: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L Alum
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 87.0%
UVA: 0.060/cm
UVA Reduction 69.8%
Settled: 3.22 NTU
70 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 78.9%
Settled: 3.45 NTU
160 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.0%
UVA: 0.042/cm
UVA Reduction 81.9%
Settled: 1.16 NTU
70 mg/L 9800
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 80.4%
Settled: 2.84 NTU

## Slide 77: Jars 54-56 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Pre & Post-KMnO4 Oxidation Applied Coagulants Alum/AdvFloc CTC-00011 /CatFloc C-378

## Slide 78: Jars 53-56: End of 5-minute flocculation (30 RPM) duration.
Pre-Oxidation Source
70 mg/L Alum
6.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 75.4%
Settled: 6.45 NTU
Post-Oxidation Source
70 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 90.8%
UVA: 0.042/cm
UVA Reduction 78.9%
Settled: 3.14 NTU
Pre-Oxidation Source
160 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 79.4%
Settled: 3.69 NTU
Post-Oxidation Source
160 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 82.4%
Settled: 0.96 NTU

## Slide 79: Jars 53-56: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 80: Jars 53-56: After 25-minutes of settling, settled water turbidity is taken.
Pre-Oxidation Source
70 mg/L Alum
6.0 mg/L C-378
Filtrate 0.08 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 75.4%
Settled: 6.45 NTU
Post-Oxidation Source
70 mg/L Alum
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 90.8%
UVA: 0.042/cm
UVA Reduction 78.9%
Settled: 3.14 NTU
Pre-Oxidation Source
160 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.10 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 79.4%
Settled: 3.69 NTU
Post-Oxidation Source
160 mg/L AdvFloc
6.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 82.4%
Settled: 0.96 NTU

## Slide 81: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 82: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 83: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 84: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 85: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 86: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732