## Slide 1: Lopez Project CA4010022 San Luis Obispo County Jar Test
by Guy Schott, P.E.
November 4, 2019

## Slide 2: Lopez Reservoir

## Slide 3: Source Water Characteristics
Source Water Characteristics
Turbidity: 1.46 NTU
pH: 8.16, Alkalinity: 250 mg/L as CaCO3
UVT: 70.5%, UVA: 0.152/cm
0.4 um Source Filtered
Turbidity: 0.15 NTU
UVT: 71.1%, UVA: 0.154/cm
0.2 um Source Filtered
Turbidity: 0.09 NTU
UVT: 71.6%, UVA: 0.145/cm
DAF(No Chlorine)
Turbidity: 0.30 NTU
UVT: 81.6%, UVA: 0.062/cm
DAF(Post Chlorine)
Turbidity: 0.40 NTU
UVT: 86.6, UVA: 0.152/cm
CFE(Post Membrane)
Turbidity: 0.06 NTU
UVT: 87.6, UVA: 0.057/cm
Post Clearwell
Turbidity: 0.06 NTU
UVT: 84.9, UVA: 0.071/cm

## Slide 4: UVT/UVA
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Coagulant Used for Jar Testing
Pro Pac 9800 (NTU Technologies)
50% ACH
50% Water
SG = 1.34
7066 (Garratt Callahan)
10 – 30% Poly Aluminum Hydroxychloride Sulfate
SG = 1.2
Pro Pac 9890 (NTU Technologies)
35-45% ACH
35-45% Water
20% Proprietary
SG = 1.25 – 1.34

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 8.11
LCA #1:
9800: 89-96 mg/L as product
pH adjusted to 7.5 with acetic acid

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Aluminum Sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Lopez Project: Jar Test 1-8 Results
Jar | 200 RPM Flash Mix seconds | 30 RPM Floc Duration minutes | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min | Settle NTU 60 min
J1 | 60 | 5 | 35 | 0.22 | 76.9 | 0.114 | 1.06 | 0.80
J2 | 60 | 5 | 85 | 0.24 | 81.6 | 0.088 | 0.68 | 0.48
J3 | 60 | 5 | 90 | 0.13 | 81.9 | 0.087 | 0.77 | 0.46
J4 | 60 | 5 | 95 | 0.22 | 81.9 | 0.087 | 0.87 | 0.61
J5 | 60 | 5 | 40 | 0.16 | 78.3 | 0.106 | 0.93 | n/a
J6 | 60 | 5 | 45 | 0.42 | 77.2 | 0.112 | 1.04 | n/a
J7 | 60 | 5 | 50 | 0.24 | 78.3 | 0.106 | 1.06 | n/a
J8 | 60 | 5 | 55 | 0.31 | 78.2 | 0.107 | 0.94 | n/a

## Slide 9: Lopez Project: Jar Test 9-16 Results
Jar | 200 RPM Flash Mix seconds | 30 RPM -Floc Duration minutes | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J9 | 60 | 5 | 40 | 0.21 | 73.4 | 0.134 | 0.86
J10 | 60 | 5 | 60 | 0.18 | 73.8 | 0.132 | 0.54
J11 | 60 | 5 | 80 | 0.17 | 74.7 | 0.127 | 0.51
J12 | 60 | 5 | 100 | 0.15 | 75.2 | 0.124 | 0.55
J13 | 60 | 5 | 120 | 0.11 | 77.6 | 0.110 | 0.31
J14 | 60 | 5 | 140 | 0.12 | 77.6 | 0.110 | 0.32
J15 | 60 | 5 | 160 | 0.11 | 78.6 | 0.105 | 0.37
J16 | 60 | 5 | 180 | 0.12 | 79.1 | 0.102 | 0.33

## Slide 10: Lopez Project: Jar Test 17-20 Results
Jar | 200 RPM Flash Mix seconds | 30 RPM Floc Duration minutes | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J17 | 60 | 5 | 15 | 0.60 | 73.6 | 0.133 | 2.46
J18 | 60 | 5 | 20 | 0.52 | 74.2 | 0.130 | 1.88
J19 | 60 | 5 | 25 | 0.52 | 75.0 | 0.125 | 2.02
J20 | 60 | 5 | 30 | 0.47 | 75.8 | 0.120 | 1.56

## Slide 11: Lopez Project: Jar Test 21-28 Results
Jar | 200 RPM Flash Mix seconds | 30 RPM Floc Duration minutes | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J21 | 60 | 5 | 20 | 0.16 | 77.9 | 0.108 | 1.54
J22 | 60 | 5 | 30 | 0.10 | 79.1 | 0.102 | 0.84
J23 | 60 | 5 | 40 | 0.10 | 80.1 | 0.096 | 0.81
J24 | 60 | 5 | 50 | 0.14 | 80.7 | 0.093 | 0.72
J25 | 60 | 5 | 60 | 0.09 | 80.6 | 0.094 | 0.61
J26 | 60 | 5 | 70 | 0.09 | 80.6 | 0.093 | 0.63
J27 | 60 | 5 | 80 | 0.16 | 81.0 | 0.092 | 0.75
J28 | 60 | 5 | 90 | 0.22 | 81.1 | 0.091 | 0.66

## Slide 12: Lopez Project: Jar Test 29-32 Results
Jar | 200 RPM Flash Mix sec | 30 RPM Floc Duration minutes | CO2 added | pH Start | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J29 | 60 | 5 | No | 8.11 | 40 | 0.08 | 81.0 | 0.092 | 0.80
J30 | 60 | 5 | Yes | 7.5 | 40 | 0.15 | 80.1 | 0.096 | 0.89
J31 | 60 | 5 | Yes | 7.0 | 40 | 0.15 | 80.0 | 0.097 | 1.24
J32 | 60 | 5 | Yes | 6.88 | 40 | 0.13 | 78.9 | 0.103 | 0.98

## Slide 13: Jars 1-4 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 14: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
35 mg/L 9800
Filtrate 0.22 NTU
UVT: 90.7%
UVA: 0.114/cm
Settled: 1.06 NTU
85 mg/L 9800
Filtrate 0.24 NTU
UVT: 81.6%
UVA: 0.088/cm
Settled: 0.68 NTU
90 mg/L 9800
Filtrate 0.13 NTU
UVT: 81.9%
UVA: 0.087/cm
Settled: 0.77 NTU
95 mg/L 9800
Filtrate 0.22 NTU
UVT: 81.9%
UVA: 0.087/cm
Settled: 0.87 NTU

## Slide 15: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 16: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L 9800
Filtrate 0.22 NTU
UVT: 76.9%
UVA: 0.114/cm
Settled: 1.06 NTU
85 mg/L 9800
Filtrate 0.24 NTU
UVT: 81.6%
UVA: 0.088/cm
Settled: 0.68 NTU
90 mg/L 9800
Filtrate 0.13 NTU
UVT: 81.9%
UVA: 0.087/cm
Settled: 0.77 NTU
95 mg/L 9800
Filtrate 0.22 NTU
UVT: 81.9%
UVA: 0.087/cm
Settled: 0.87 NTU

## Slide 17: Jars 5-8 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 18: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
40 mg/L 9800
Filtrate 0.16 NTU
UVT: 78.6%
UVA: 0.106/cm
Settled: 0.96 NTU
45 mg/L 9800
Filtrate 0.42 NTU
UVT: 77.2%
UVA: 0.112/cm
Settled: 1.04 NTU
50 mg/L 9800
Filtrate 0.24 NTU
UVT: 78.2%
UVA: 0.106/cm
Settled: 1.06 NTU
55 mg/L 9800
Filtrate 0.24 NTU
UVT: 78.2%
UVA: 0.106/cm
Settled: 1.06 NTU

## Slide 19: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 20: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
40 mg/L 9800
Filtrate 0.16 NTU
UVT: 78.6%
UVA: 0.106/cm
Settled: 0.96 NTU
45 mg/L 9800
Filtrate 0.42 NTU
UVT: 77.2%
UVA: 0.112/cm
Settled: 1.04 NTU
50 mg/L 9800
Filtrate 0.24 NTU
UVT: 78.2%
UVA: 0.106/cm
Settled: 1.06 NTU
55 mg/L 9800
Filtrate 0.24 NTU
UVT: 78.2%
UVA: 0.106/cm
Settled: 1.06 NTU

## Slide 21: Jars 9-12 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 7066

## Slide 22: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
40 mg/L 7066
Filtrate 0.21 NTU
UVT: 73.4%
UVA: 0.134/cm
Settled: 0.86 NTU
60 mg/L 7066
Filtrate 0.18 NTU
UVT: 73.8%
UVA: 0.132/cm
Settled: 0.54 NTU
80 mg/L 7066
Filtrate 0.17 NTU
UVT: 74.7%
UVA: 0.127/cm
Settled: 0.51 NTU
100 mg/L 7066
Filtrate 0.15 NTU
UVT: 75.2%
UVA: 0.124/cm
Settled: 0.55 NTU

## Slide 23: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 24: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
40 mg/L 7066
Filtrate 0.21 NTU
UVT: 73.4%
UVA: 0.134/cm
Settled: 0.86 NTU
60 mg/L 7066
Filtrate 0.18 NTU
UVT: 73.8%
UVA: 0.132/cm
Settled: 0.54 NTU
80 mg/L 7066
Filtrate 0.17 NTU
UVT: 74.7%
UVA: 0.127/cm
Settled: 0.51 NTU
100 mg/L 7066
Filtrate 0.15 NTU
UVT: 75.2%
UVA: 0.124/cm
Settled: 0.55 NTU

## Slide 25: Jars 13-16 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 7066

## Slide 26: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
120 mg/L 7066
Filtrate 0.11 NTU
UVT: 77.6%
UVA: 0.110/cm
Settled: 0.31 NTU
140 mg/L 7066
Filtrate 0.12 NTU
UVT: 77.6%
UVA: 0.110/cm
Settled: 0.32 NTU
160 mg/L 7066
Filtrate 0.11 NTU
UVT: 78.6%
UVA: 0.105/cm
Settled: 0.37 NTU
180 mg/L 7066
Filtrate 0.12 NTU
UVT: 79.1%
UVA: 0.102/cm
Settled: 0.33 NTU

## Slide 27: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 28: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
120 mg/L 7066
Filtrate 0.11 NTU
UVT: 77.6%
UVA: 0.110/cm
Settled: 0.31 NTU
140 mg/L 7066
Filtrate 0.12 NTU
UVT: 77.6%
UVA: 0.110/cm
Settled: 0.32 NTU
160 mg/L 7066
Filtrate 0.11 NTU
UVT: 78.6%
UVA: 0.105/cm
Settled: 0.37 NTU
180 mg/L 7066
Filtrate 0.12 NTU
UVT: 79.1%
UVA: 0.102/cm
Settled: 0.33 NTU

## Slide 29: Jars 17-20 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 30: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
15 mg/L 9800
Filtrate 0.60 NTU
UVT: 73.6%
UVA: 0.133/cm
Settled: 2.46 NTU
20 mg/L 9800
Filtrate 0.52 NTU
UVT: 74.2%
UVA: 0.130/cm
Settled: 1.88 NTU
25 mg/L 9800
Filtrate 0.52 NTU
UVT: 75.0%
UVA: 0.125/cm
Settled: 2.02 NTU
30 mg/L 9800
Filtrate 0.47 NTU
UVT: 75.8%
UVA: 0.120/cm
Settled: 1.56 NTU

## Slide 31: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 32: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
15 mg/L 9800
Filtrate 0.60 NTU
UVT: 73.6%
UVA: 0.133/cm
Settled: 2.46 NTU
20 mg/L 9800
Filtrate 0.52 NTU
UVT: 74.2%
UVA: 0.130/cm
Settled: 1.88 NTU
25 mg/L 9800
Filtrate 0.52 NTU
UVT: 75.0%
UVA: 0.125/cm
Settled: 2.02 NTU
30 mg/L 9800
Filtrate 0.47 NTU
UVT: 75.8%
UVA: 0.120/cm
Settled: 1.56 NTU

## Slide 33: Jars 21-24 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 34: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
20 mg/L 9890
Filtrate 0.16 NTU
UVT: 77.9%
UVA: 0.108/cm
Settled: 1.54 NTU
30 mg/L 9890
Filtrate 0.10 NTU
UVT: 79.1%
UVA: 0.102/cm
Settled: 0.84 NTU
40 mg/L 9890
Filtrate 0.10 NTU
UVT: 80.1%
UVA: 0.096/cm
Settled: 0.81 NTU
50 mg/L 9890
Filtrate 0.14 NTU
UVT: 80.7%
UVA: 0.093/cm
Settled: 0.72 NTU

## Slide 35: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 36: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L 9890
Filtrate 0.16 NTU
UVT: 77.9%
UVA: 0.108/cm
Settled: 1.54 NTU
30 mg/L 9890
Filtrate 0.10 NTU
UVT: 79.1%
UVA: 0.102/cm
Settled: 0.84 NTU
40 mg/L 9890
Filtrate 0.10 NTU
UVT: 80.1%
UVA: 0.096/cm
Settled: 0.81 NTU
50 mg/L 9890
Filtrate 0.14 NTU
UVT: 80.7%
UVA: 0.093/cm
Settled: 0.72 NTU

## Slide 37: Jars 25-28 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 38: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
60 mg/L 9890
Filtrate 0.09 NTU
UVT: 80.6%
UVA: 0.094/cm
Settled: 0.61 NTU
70 mg/L 9890
Filtrate 0.09 NTU
UVT: 80.8%
UVA: 0.093/cm
Settled: 0.63 NTU
80 mg/L 9890
Filtrate 0.16 NTU
UVT: 81.0%
UVA: 0.092/cm
Settled: 0.75 NTU
90 mg/L 9890
Filtrate 0.22 NTU
UVT: 81.1%
UVA: 0.091/cm
Settled: 0.66 NTU

## Slide 39: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 40: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L 9890
Filtrate 0.09 NTU
UVT: 80.6%
UVA: 0.094/cm
Settled: 0.61 NTU
70 mg/L 9890
Filtrate 0.09 NTU
UVT: 80.8%
UVA: 0.093/cm
Settled: 0.63 NTU
80 mg/L 9890
Filtrate 0.16 NTU
UVT: 81.0%
UVA: 0.092/cm
Settled: 0.75 NTU
90 mg/L 9890
Filtrate 0.22 NTU
UVT: 81.1%
UVA: 0.091/cm
Settled: 0.66 NTU

## Slide 41: Jars 29-32 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800 w/CO2

## Slide 42: Jars 29-32: End of 5-minute flocculation (30 RPM) duration.
Added CO2 (No)
pHs: 8.11
40 mg/L 9890
Filtrate 0.08 NTU
UVT: 81.0%
UVA: 0.092/cm
Settled: 0.80 NTU
Added CO2 (Yes)
pHs: 7.5
40 mg/L 9890
Filtrate 0.15 NTU
UVT: 80.1%
UVA: 0.096/cm
Settled: 0.89 NTU
Added CO2 (Yes)
pHs: 7.0
40 mg/L 9890
Filtrate 0.15 NTU
UVT: 80.0%
UVA: 0.097/cm
Settled: 1.24 NTU
Added CO2 (Yes)
pHs: 6.88
40 mg/L 9890
Filtrate 0.13 NTU
UVT: 78.9%
UVA: 0.103/cm
Settled: 0.98 NTU

## Slide 43: Jars 28-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 44: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
Added CO2 (No)
pHs: 8.11
40 mg/L 9890
Filtrate 0.08 NTU
UVT: 81.0%
UVA: 0.092/cm
Settled: 0.80 NTU
Added CO2 (Yes)
pHs: 7.5
40 mg/L 9890
Filtrate 0.15 NTU
UVT: 80.1%
UVA: 0.096/cm
Settled: 0.89 NTU
Added CO2 (Yes)
pHs: 7.0
40 mg/L 9890
Filtrate 0.15 NTU
UVT: 80.0%
UVA: 0.097/cm
Settled: 1.24 NTU
Added CO2 (Yes)
pHs: 6.88
40 mg/L 9890
Filtrate 0.13 NTU
UVT: 78.9%
UVA: 0.103/cm
Settled: 0.98 NTU

## Slide 45: Jar Testing for 1-Liter Jars: General Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 46: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 47: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 48: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 49: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 50: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732