## Slide 1: Tracer Studies And Disinfection
Guy Schott, P.E.
Presented to
AWWA – Sacramento, CA
March 27, 2019

## Slide 2: Learning Objectives
Purpose of a tracer study
Water age distribution
Disinfection exposure time
CT disinfection (pathogen delivered dose)
Log inactivation
Baffling Factor (BF)
Tracer test preparation
Hydraulic efficiencies for different reactors
Discussion

## Slide 3: Purpose of a Tracer Study
To determine the hydraulic or disinfectant exposure time of water through one or more reactors.
Performed by the addition of a nonreactive chemical (tracer, marker).

## Slide 4
60% of water age is 100 min or more
90% of water age is 62 min or more
10%
40%

## Slide 5: Disinfection Exposure Time (t10)
Based on the time it takes for 10% of the total water entering a reactor to be the first to exit the reactor. Determined via tracer study.

## Slide 6: Disinfectant Exposure Time
Related to:
  Reactor configuration
  (inlet/outlet, baffles, L:W)
  Water Depth
  Working volume
  Flow rate
  Temperature gradient
  Hydraulic mixing

## Slide 7: Delivered Dose to Pathogen (Ct)
Delivered Dose, “Ct”
  “C” is the disinfectant residual (mg/L)
  “t” is the disinfectant exposure or contact time (minutes)
C x t = mg/L * min, delivered dose
Cl2
Cl2
Cl2
Cl2
Cl2

## Slide 8: Disinfection Log Inactivation
Giardia cyst log inactivation is based on the Delivered Dose, “Ct” and associated
pH
Disinfectant residual
Temperature
Virus log inactivation is based on the Delivered Dose, “Ct” and associated
Disinfectant residual
Temperature
Parameters are looked up in EPA Ct tables to determine the log inactivation.

## Slide 9: Baffling Factor (BF)
Generated from Tracer Study:
t10 = disinfectant exposure time
HRT = hydraulic residence time = Volume/flow
Baffling Factor (BF) = t10 / HRT
0 < BF < 1
BF is applied to the disinfection contact basin’s operational HRT to determine contact time (t10, minutes).
Calculated daily treatment plant disinfectant exposure time:
t10_cal = BF x HRT

## Slide 10: Tracer Test Preparation
Reactor Process to Evaluate
Tracer methods
Tracer material
Tracer dosage
Test flows and reactor operating level
Test duration
Chemical feed pump
Sample locations
Sample frequency
Communication between parties involved

## Slide 11: 1. Tracer Methods
Chart: Step-Dose Curve
Chart: Slug-Dose Curve
A continuous tracer feed added throughout test.
Adding the entire amount of tracer at the beginning of test.

## Slide 12: Tracer Test Methods
Step-Dose Method
A continuous tracer feed added throughout test.
Slug-Dose Method
Adding the entire amount of tracer at the beginning of test.
ti…..
Tracer
Tracer
Q1
Q2
Cl2
Cl2
Chlorine Contact Basin

## Slide 13: Model Step-Dose Curve
Chart: Step-Dose Curve

## Slide 14: Model Slug-Dose Curve
Chart: Slug-Dose Curve

## Slide 15: Actual Slug-Dose Curve
Chart: Slug-Dose Curve

## Slide 16: 2. Tracer Material
Fluoride (F)
  Liquid (H2SiF6 Hydrofluorosilicic Acid)
  Dry (NaF)
    15 gal NaF mix solution : 1 gal H2SiF6
Lithium Chloride (Li)
Others (NaCl, CaCl2), dry or liquid
Tracer should be non-reactive

## Slide 17: 3. Dosage
Step-Dose
  Fluoride: 2 to 4.0 mg/L as F
  Lithium: 0.5 mg/L
  Chloride/Na/Ca: Dependent on background constituents and any secondary standards

## Slide 18: Slug-Dose Test How Much Tracer to Add
  Estimate BF
  Calculate amount of tracer mass needed for associated dispersion concentration.
  For lower or higher peak concentration, apply factor to dispersion concentration.
.
t10/HRT (BF) | Calculated Dispersion Concentration in Basin | Tracer Study Peak Concentration (estimated)
0.24 | 1.35 | 1.0
0.34 | 1.23 | 1.0
0.42 | 1.12 | 1.0
0.51 | 0.95 | 1.0
0.61 | 0.76 | 1.0
0.70 | 0.58 | 1.0

## Slide 19: 4A. Test Flows and Operating Level
One Test: Normal operating flow and clearwell level.
Two Tests: Summer/winter flows and clearwell levels.
Three Tests: High/mid/low flows and normal operating clearwell levels.
Notes: Think of an in-line motionless static mixer. The higher the flow, greater mixing.

## Slide 20: 4B. Test Flows and Operating Level
Baffle tanks –
  Higher flow, results in greater mixing (>Reynolds number & BF)
  At a given flow, increase tank volume (<Reynolds number & BF)
Non-baffled tanks -
  Less predicable
  Temperature gradient can result in less mixing (<BF), greater short-circuiting.
  At a given flow, increase/decrease in tank volume (? Increase/decrease in BF)
Notes: Think of an in-line motionless static mixer. The higher the flow, greater mixing.

## Slide 21: 5A. Test Duration
May vary from < 1 HRT to 4 HRT (site specific & predicted BF)
For full tracer recovery (slug-dose) and steady-state tracer (step-dose)
  2.5 - 4 HRT duration

## Slide 22: 5B. Test Duration - When HRT is very long
Modified the Step-Dose method
Test is completed in less than 1 HRT
Measurements of tracer inlet and outlet
Inlet measurements:
  Flow into 5-gallon bucket over several minutes to ensure average applied tracer dosage is measured. Take sample out of bucket.
  Dump bucket and start over with next sample
  Average inlet sample results to determine applied dosage
Outlet measurements:
  Sample duration < HRT
Notes: If inlet to reactor cannot be measured, then physical chemical drawdown is required. Modified Slug-dose could be acceptable.

## Slide 23: Modified Step-Dose Method
Clearwell
Inlet
Sampling
Outlet
Sampling
All sampling is conducted to 1 x HRT or less
Tracer

## Slide 24: Actual Modified Step-Dose Test Curve
Chart: Step-Dose Curve
| 0 | 4.2519999999999995E-2 | 9.5670000000000005E-2 | 0.11692999999999999 | 0.13818999999999998 | 0.15944999999999998 | 0.18070999999999995 | 0.20196999999999996 | 0.22322999999999996 | 0.24448999999999996 | 0.26574999999999993 | 0.28700999999999993 | 0.30826999999999993 | 0.32952999999999993 | 0.35078999999999988 | 0.37204999999999988 | 0.38267999999999991 | 0.39330999999999994 | 0.40393999999999997 | 0.41456999999999999 | 0.42519999999999997 | 0.43583000000000005 | 0.44646000000000002 | 0.45709000000000005 | 0.46772000000000002 | 0.47835000000000011 | 0.48898000000000014 | 0.49961000000000011 | 0.51024000000000014 | 0.52087000000000017 | 0.53150000000000019 | 0.54213000000000022
 | 0 | 0 | 0 | 0.0011765 | 0.00080882 | 0.00040441 | 0.00095588 | 0.00047794 | 0.00047794 | 0.0026838 | 0.00625 | 0.0088235 | 0.0125 | 0.016544 | 0.025 | 0.031985 | 0.035294 | 0.045588 | 0.047794 | 0.054044 | 0.057721 | 0.061029 | 0.067647 | 0.070956 | 0.079412 | 0.090074 | 0.095221 | 0.10478 | 0.11029 | 0.11875 | 0.12537 | 0.13456

## Slide 25: 6. Chemical Feed Pump
Select chemical feed pump capacity based on plant flow and mL/min dosage range.
Before tracer test, prime and test feed pump to ensure it works and stays on during duration of test.
For slug-dose test, may be appropriate to temporarily shut down treatment plant for 2-5 minutes to inject tracer material and then start plant (site-specific).

## Slide 26: 7. Sample Frequency
Sample distribution frequency is depended on baffling factor resolution goal around critical sampling region.
Example:
    Goal – e.g., measure to the nearest 0.02 baffling factor (BF).
    HRT = 150 minutes
    Sample Frequency Critical Region
    0.02 • HRT = 0.02 • 150 min = 3 minutes
Critical region – is the area under curve where t10 occurs for a Step-Dose curve.

## Slide 27: 8. Sample Locations
Reactor outlet
Modified Step-Dose, inlet/outlet
  Use 5 gallon bucket for inlet sampling to obtain average inlet tracer dosage
  Take sample out of bucket
  Dump bucket and start over

## Slide 28: 9. Communications
Plant personnel
Regulatory agency
Firm doing the tracer study
By phone, email and/or written report

## Slide 29: When flows are not at steady-state
Variable outlet flow
  Modified step-dose method
  Take cumulative treated water volume (V10, gallons) from time zero (to) to t10
  Divide cumulative volume (V10) by average working volume (V10/V) = BF
BF= V10/V from tracer test (based on volume)
  V10: The volume of water that has exited the reactor from to to t10 when 10% of the tracer mass has exited the reactor.
  V: Average operating Clearwell volume of water during tracer test from to to t10.

## Slide 30: Reactors – Chlorine Contactors
Circular
Tanks
Rectangular Tanks,
Serpentine Flow
Top View
BF (0.05-0.2)
BF (0.3-0.4), L:W = 12
BF (0.4-0.45), L:W = 16
BF (0.6-0.7), L:W = 52
BF is depended on reactor design, volume, water depth, flow and temperature gradient
L:W is the total travel length of water divided by channel width or pipe diameter.

## Slide 31: Determining L:W ratio
Length is longest flow path (red line).
Width is the average channel width for each flow path.
Inlet
Outlet

## Slide 32: Determining L:W ratio
Length is longest flow path (red line).
Width is the average channel width for each flow path.
Inlet
Outlet

## Slide 33
Chart: Length-to-Width Ratios vs. t10/HRT Baffled Tanks

## Slide 34: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
For Tracer Study Database and/or Results:
https://www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Guy.Schott@waterboards.ca.gov
707-576-2732