## Slide 1: Ione Amador Water Agency CA0310002, Amador County, Jar Test
by Guy Schott, P.E. April 10, 2023

## Slide 2: Ryan adding coag.

## Slide 3: Ione AWA Source & Treated Water Characteristics, April 10, 2023
Source – Ione Reservoir
pH: 7.35 – 7.49
Alkalinity: 20 mg/L as CaCO3
Turbidity: 1.89 NTU
UVT: 86.0%,
UVA: 0.065/cm
0.4 um Filtered
Turbidity: 0.40 NTU
UVT: 86.9%,
UVA: 0.060/cm
Plant Filtrate Water
0.05 NTU
UVT: 95.5%,
UVA: 0.019/cm
Plant Filtrate Post Chlorine Water
0.08 NTU
UVT: 96.5%,
UVA: 0.015/cm

## Slide 4: Applied Coagulants for Jar Testing (1)
SWT 8809 (Sterling Water Technologies)
25% Aluminum Chlorohydrate
25% pDADMAC
50% Water
11.81% Al2O3
6.25% Al
83% Basicity
SG = 1.19-1.33
NSF limit: 20 mg/L as Product
Product dose 6.5 mg/L = 1.62 mg/L pDADMAC
961 (NTU Technologies)
32% Polyaluminum Hydroxychlorosulfate
2% pDADMAC (blend?)
66% Water
SG = 1.2-1.24
NSF limit: 255 mg/L as Product

## Slide 5: Applied Coagulants for Jar Testing (2)
NTU Technologies
Pro Pac 9810
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 20 mg/L = 0.5 mg/L polyamines active
905 (NTU Technologies)
45-55% Aluminum Chlorohydrate (~49%)
2% pDADMAC (blend?)
45-55% Water
SG = 1.2 – 1.34
NSF limit: 255 mg/L as Product
960 (NTU Technologies)
33% Polyaluminum Hydroxychlorosulfate
67% Water
SG = 1.2 – 1.3
NSF limit: 250 mg/L as Product

## Slide 6: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 7: Cl2 Decay Rate
Chart: Source Water %UVA Reduction (NaOCl = 2.5 mg/L Spiked)
| 0 | 12 | 36 | 60 | 120
 | 0 | 0.24194 | 0.27419 | 0.32258 | 0.33871

## Slide 8: UVA Reduction
Chart: Source Water %UVA Reduction (NaOCl = 2.5 mg/L Spiked)
| 0 | 12 | 36 | 60 | 120
%UVT Reduction | 0 | 0.24194 | 0.27419 | 0.32258 | 0.33871
UVA/cm | 0.062 | 0.047 | 0.045 | 0.042 | 0.041

## Slide 9: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.35-7.49
LCA #1: 8809 [Al][PY]
~4.2 mg/L as product

## Slide 10: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 11: Ione AWA: TTHMs Laboratory Results NaOCl dose after filtration: 2 mg/L (Hold Time 2 days)
Jar # | Pre-NaOCl mg/L | 961 mg/L | SWT 8809 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | TTHM ug/L | Cl2 Residual mg/L
1 | 1.5 | - | 6.5 | 0.05 | 94.3 | 0.025 | 58.3 | 69 | 0.07
2 | 0 | 29 | - | 0.04 | 96.1 | 0.016 | 73.3 | 43 | 0.31

## Slide 12: Jar Test – Filtrate Water Spiked with 2 mg/L NaOCl Plant Coagulant Dose vs. Optimum Dose and Coagulant
Chart: Chlorine Residual Over Time
| 0 | 0.41666666666666669 | 0.91666666666666663 | 1.4583333333333333 | 1.9166666666666667 | 2.4166666666666665 | 3.0208333333333335 | 3.4583333333333335 | 3.9583333333333335 | 4.458333333333333 | 4.916666666666667 | 5.458333333333333 | 6.020833333333333
Pre-NaOCl: 1.5 mg/L; Coag: 8809 = 6.5 mg/L: UVA: 0.025/cm, UVT: 94.3% | 1.46 | 0.49 | 0.31 | 0.21 | 0.15 | 0.09 | 0.05 | 0.03
Coag: 961: 29 mg/L; UVA: 0.016/cm, UVT: 96.1% | 1.35 | 0.52 | 0.42 | 0.38 | 0.3 | 0.24 | 0.2 | 0.19 | 0.13 | 0.12 | 0.09 | 0.08 | 0.04
TTHM: 69 ug/L,
TTHM: 43 ug/L,

## Slide 13: Ione AWA; Source: Ione Reservoir Summary of Optimum Dose/Coagulants for Tested Products
Coag Product | NaOCl mg/L | Coag Dose mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Coagulant Max Use, mg/L
8809 | 1.5 | 6.5 | 0.06 | 94.5 | 0.024 | 60.0 | 1.82 | 7.24 | 20
8809 | 1.5 | 6.5 | 0.05 | 94.3 | 0.025 | 58.3 | 3.28 | - | 20
905 | 1.5 | 12 | 0.04 | 95.5 | 0.019 | 68.3 | 2.07 | 7.17 | 255
905 | 1.5 | 15 | 0.03 | 96.1 | 0.017 | 71.7 | 1.42 | 7.16 | 255
9810 | 1.5 | 12 | 0.04 | 95.6 | 0.019 | 68.3 | 1.81 | 7.17 | 200
9810 | 1.5 | 12 | 0.03 | 95.8 | 0.018 | 70.0 | 1.72 | - | 200
961 | 1.5 | 29 | 0.04 | 95.6 | 0.019 | 68.3 | 0.95 | 6.94 | 255
961 | 1.5 | 29 | 0.03 | 95.7 | 0.018 | 70.0 | 0.87 | 6.89 | 255
961 | 0 | 29 | 0.04 | 96.1 | 0.016 | 73.3 | 1.76 | - | 255

## Slide 14: Ione AWA; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | NaOCl mg/L | 8809 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 0 | 3.5 | 0.15 | 92.7 | 0.032 | 46.7 | 2.54
J2 | 0 | 4.0 | 0.08 | 93.5 | 0.028 | 53.3 | 2.44
J3 | 0 | 4.5 | 0.16 | 93.2 | 0.030 | 50.0 | 2.47
J4 | 0 | 5.0 | 0.08 | 94.0 | 0.026 | 56.7 | 2.41
J5 | 1.5 | 3.5 | 0.07 | 93.7 | 0.028 | 53.3 | 2.28
J6 | 1.5 | 4.0 | 0.12 | 93.7 | 0.027 | 55.0 | 2.47
J7 | 1.5 | 4.5 | 0.06 | 94.0 | 0.026 | 56.7 | -
J8 | 1.5 | 5.0 | 0.10 | 94.1 | 0.026 | 56.7 | -

## Slide 15: Ione AWA; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | 960 mg/L | 961 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 5 | - | 0.43 | 87.8 | 0.056 | 6.7 | 1.72
J10 | 10 | - | 0.47 | 88.9 | 0.050 | 16.7 | 1.92
J11 | 15 | - | 0.06 | 93.4 | 0.029 | 51.7 | 1.92
J12 | 20 | - | 0.06 | 93.7 | 0.028 | 53.3 | 1.82
J13 | - | 14 | 0.09 | 93.4 | 0.029 | 51.7 | 1.96
J14 | - | 19 | 0.05 | 94.0 | 0.026 | 56.7 | 1.34
J15 | - | 24 | 0.05 | 94.3 | 0.025 | 58.3 | 1.21
J16 | - | 29 | 0.04 | 94.4 | 0.024 | 60.0 | 0.93

## Slide 16: Ione AWA; Jar Test 17 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | NaOCl mg/L | 8809 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 1.5 | 5.0 | 0.11 | 93.9 | 0.026 | 56.7 | 3.48
J18 | 1.5 | 5.5 | 0.14 | 94.0 | 0.026 | 56.7 | 3.45
J19 | 1.5 | 6.0 | 0.18 | 93.8 | 0.027 | 55.0 | 3.36
J20 | 1.5 | 6.5 | 0.07 | 94.5 | 0.024 | 60.0 | 3.39
J21 | 0 | 6.5 | 0.21 | 93.0 | 0.031 | 48.3 | 2.8
J22 | 1.5 | 6.5 | 0.06 | 94.1 | 0.026 | 56.7 | 3.1
J23 | 1.5 | 7.0 | 0.21 | 93.4 | 0.029 | 51.7 | 3.1
J24 | 1.5 | 7.5 | 0.09 | 94.1 | 0.026 | 56.7 | 2.6

## Slide 17: Ione AWA; Jar Test 25 - 28 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | NaOCl mg/L | 8809 mg/L | 961 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 1.5 | 6.5 | - | 0.22 | 94.0 | 0.026 | 56.7 | 3.37
J26 | 1.5 | 6.5 | - | 0.05 | 94.3 | 0.025 | 58.3 | 3.28
J27 | 0 | - | 29 | 0.04 | 96.1 | 0.016 | 73.3 | 1.76
J28 | 0 | - | 29 | 0.06 | 95.9 | 0.018 | 70.0 | 1.52

## Slide 18: Ione AWA; Jar Test 29 - 36 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | NaOCl mg/L | 8809 mg/L | 961 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J29 | 0 | 6.5 | - | 0.16 | 93.2 | 0.030 | 50.0 | 2.28 | 7.33 | 18
J30 | 1.5 | 6.5 | - | 0.06 | 94.3 | 0.025 | 58.3 | 2.42 | 7.30 | 19
J31 | 0 | - | 29 | 0.04 | 95.8 | 0.018 | 70.0 | 1.38 | 6.86 | 16
J32 | 1.5 | - | 29 | 0.04 | 95.7 | 0.018 | 70.0 | 0.95 | 6.87 | 17
J33 | 0 | - | 29 | 0.03 | 94.8 | 0.023 | 61.7 | 0.91 | 6.89 | -
J34 | 1.5 | - | 29 | 0.03 | 95.7 | 0.018 | 70.0 | 0.87 | 6.89 | -
J35 | 0 | - | 34 | 0.03 | 95.8 | 0.018 | 70.0 | 1.08 | 6.81 | -
J36 | 1.5 | - | 34 | 0.03 | 96.0 | 0.017 | 71.7 | 0.95 | 6.86 | -

## Slide 19: Ione AWA; Jar Test 37 - 44 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | NaOCl mg/L | 905 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J37 | 1.5 | 5 | 0.06 | 93.8 | 0.027 | 55.0 | 1.09 | 7.35 | 19.5
J38 | 1.5 | 10 | 0.03 | 95.6 | 0.019 | 68.3 | 1.32 | 7.23 | 18.5
J39 | 1.5 | 15 | 0.03 | 96.1 | 0.017 | 71.7 | 1.42 | 7.16 | 18.3
J40 | 1.5 | 20 | 0.03 | 96.4 | 0.015 | 75.0 | 1.19 | 7.15 | 19
J41 | 0 | 12 | 0.03 | 95.6 | 0.019 | 68.3 | 1.54 | - | -
J42 | 1.5 | 12 | 0.03 | 95.7 | 0.018 | 70.0 | 1.80 | - | -
J43 | 0 | 15 | 0.08 | 95.4 | 0.020 | 66.7 | 1.66 | - | -
J44 | 1.5 | 15 | 0.04 | 95.9 | 0.017 | 71.7 | 1.48 | - | -

## Slide 20: Ione AWA; Jar Test 45 - 48 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | NaOCl mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J45 | 1.5 | 6 | 0.04 | 94.5 | 0.024 | 60.0 | 1.43
J46 | 1.5 | 9 | 0.05 | 95.2 | 0.021 | 65.0 | 1.98
J47 | 1.5 | 12 | 0.03 | 95.8 | 0.018 | 70.0 | 1.72
J48 | 1.5 | 15 | 0.03 | 96.0 | 0.017 | 71.7 | 1.84

## Slide 21: Ione AWA; Jar Test 49 - 52 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | NaOCl mg/L | 8809 mg/L | 905 mg/L | 9810 mg/L | 961 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH
J49 | 1.5 | 6.5 | - | - | - | 0.06 | 94.5 | 0.024 |  | 1.82 | 7.24
J50 | 1.5 | - | 12 | - | - | 0.04 | 95.5 | 0.019 |  | 2.07 | 7.17
J51 | 1.5 | - | - | 12 | - | 0.04 | 95.6 | 0.019 |  | 1.81 | 7.17
J52 | 1.5 | - | - | - | 29 | 0.04 | 95.6 | 0.019 |  | 0.95 | 6.94

## Slide 22: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 8809

## Slide 23: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
0 mg/L NaOCl
3.5 mg/L 8809
Filtrate: 0.15 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 46.7%
Settled: 2.54 NTU
0 mg/L NaOCl
4.0 mg/L 8809
Filtrate: 0.08 NTU
UVT: 93.5%
UVA: 0.028/cm
UVA Reduction: 53.3%
Settled: 2.44 NTU
0 mg/L NaOCl
4.5 mg/L 8809
Filtrate: 0.16 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 50.0%
Settled: 2.47 NTU
0 mg/L NaOCl
5.0 mg/L 961
Filtrate: 0.08 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 2.41 NTU

## Slide 24: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
3.5 mg/L 8809
Filtrate: 0.15 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 46.7%
Settled: 2.54 NTU
0 mg/L NaOCl
4.0 mg/L 8809
Filtrate: 0.08 NTU
UVT: 93.5%
UVA: 0.028/cm
UVA Reduction: 53.3%
Settled: 2.44 NTU
0 mg/L NaOCl
4.5 mg/L 8809
Filtrate: 0.16 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 50.0%
Settled: 2.47 NTU
0 mg/L NaOCl
5.0 mg/L 961
Filtrate: 0.08 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 2.41 NTU

## Slide 25: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 8809

## Slide 26: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
1.5 mg/L NaOCl
3.5 mg/L 8809
Filtrate: 0.07 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 53.3%
Settled: 2.28 NTU
1.5 mg/L NaOCl
4.0 mg/L 8809
Filtrate: 0.12 NTU
UVT: 93.7%
UVA: 0.027/cm
UVA Reduction: 55.0%
Settled: 2.47 NTU
1.5 mg/L NaOCl
4.5 mg/L 8809
Filtrate: 0.06 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: - NTU
1.5 mg/L NaOCl
5.0 mg/L 8809
Filtrate: 0.10 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: - NTU

## Slide 27: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 960

## Slide 28: Jars 9-12: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
0 mg/L NaOCl
5 mg/L 960
Filtrate: 0.43 NTU
UVT: 93.7%
UVA: 0.056/cm
UVA Reduction: 6.7%
Settled: 1.72 NTU
0 mg/L NaOCl
10 mg/L 960
Filtrate: 0.47 NTU
UVT: 88.9%
UVA: 0.050/cm
UVA Reduction: 16.7%
Settled: 1.92 NTU
0 mg/L NaOCl
15 mg/L 960
Filtrate: 0.06 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction: 51.7%
Settled: 1.92 NTU
0 mg/L NaOCl
20 mg/L 960
Filtrate: 0.06 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 53.3%
Settled: 1.82 NTU

## Slide 29: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
5 mg/L 960
Filtrate: 0.43 NTU
UVT: 93.7%
UVA: 0.056/cm
UVA Reduction: 6.7%
Settled: 1.72 NTU
0 mg/L NaOCl
10 mg/L 960
Filtrate: 0.47 NTU
UVT: 88.9%
UVA: 0.050/cm
UVA Reduction: 16.7%
Settled: 1.92 NTU
0 mg/L NaOCl
15 mg/L 960
Filtrate: 0.06 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction: 51.7%
Settled: 1.92 NTU
0 mg/L NaOCl
20 mg/L 960
Filtrate: 0.06 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 53.3%
Settled: 1.82 NTU

## Slide 30: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 961

## Slide 31: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
15 mg/L 961
Filtrate: 0.09 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction: 51.7%
Settled: 1.96 NTU
0 mg/L NaOCl
20 mg/L 961
Filtrate: 0.05 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 1.34 NTU
0 mg/L NaOCl
25 mg/L 961
Filtrate: 0.05 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 58.3%
Settled: 1.21 NTU
0 mg/L NaOCl
30 mg/L 961
Filtrate: 0.04 NTU
UVT: 94.4%
UVA: 0.024/cm
UVA Reduction: 60.0%
Settled: 0.93 NTU

## Slide 32: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 8809

## Slide 33: Jars 17-20: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
1.5 mg/L NaOCl
5.0 mg/L 8809
Filtrate: 0.11 NTU
UVT: 93.9%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 3.48 NTU
1.5 mg/L NaOCl
5.5 mg/L 8809
Filtrate: 0.14 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 3.45 NTU
1.5 mg/L NaOCl
6.0 mg/L 8809
Filtrate: 0.18 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction: 55.0%
Settled: 3.36 NTU
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.07 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 60.0%
Settled: 3.39 NTU

## Slide 34: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
1.5 mg/L NaOCl
5.0 mg/L 8809
Filtrate: 0.11 NTU
UVT: 93.9%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 3.48 NTU
1.5 mg/L NaOCl
5.5 mg/L 8809
Filtrate: 0.14 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 3.45 NTU
1.5 mg/L NaOCl
6.0 mg/L 8809
Filtrate: 0.18 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction: 55.0%
Settled: 3.36 NTU
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.07 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 60.0%
Settled: 3.39 NTU

## Slide 35: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 8809

## Slide 36: Jars 21-24: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
0 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.21 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction: 48.3%
Settled: 2.8 NTU
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.06 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 3.1 NTU
1.5 mg/L NaOCl
7.0 mg/L 8809
Filtrate: 0.21 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction: 51.7%
Settled: 3.1 NTU
1.5 mg/L NaOCl
7.5 mg/L 8809
Filtrate: 0.09 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 2.6 NTU

## Slide 37: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.21 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction: 48.3%
Settled: 2.8 NTU
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.06 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 3.1 NTU
1.5 mg/L NaOCl
7.0 mg/L 8809
Filtrate: 0.21 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction: 51.7%
Settled: 3.1 NTU
1.5 mg/L NaOCl
7.5 mg/L 8809
Filtrate: 0.09 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 2.6 NTU

## Slide 38: Jars 25-28 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 8809 & 961

## Slide 39: Jars 25-28: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.22 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 3.37 NTU
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.05 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 58.3%
Settled: 3.28 NTU
0 mg/L NaOCl
30 mg/L 961
Filtrate: 0.04 NTU
UVT: 96.1%
UVA: 0.016/cm
UVA Reduction: 73.3%
Settled: 1.76 NTU
0 mg/L NaOCl
30 mg/L 961
Filtrate: 0.06 NTU
UVT: 95.9%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.52 NTU

## Slide 40: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.22 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 56.7%
Settled: 3.37 NTU
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.05 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 58.3%
Settled: 3.28 NTU
0 mg/L NaOCl
30 mg/L 961
Filtrate: 0.04 NTU
UVT: 96.1%
UVA: 0.016/cm
UVA Reduction: 73.3%
Settled: 1.76 NTU
0 mg/L NaOCl
30 mg/L 961
Filtrate: 0.06 NTU
UVT: 95.9%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.52 NTU

## Slide 41: Jars 29-32 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 8809 & 961

## Slide 42: Jars 29-32: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
0 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.16 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 50.0%
Settled: 2.28 NTU
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.06 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 58.3%
Settled: 2.42 NTU
0 mg/L NaOCl
29 mg/L 961
Filtrate: 0.04 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.38 NTU
1.5 mg/L NaOCl
29 mg/L 961
Filtrate: 0.04 NTU
UVT: 95.7%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 0.95 NTU

## Slide 43: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.16 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 50.0%
Settled: 2.28 NTU
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.06 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 58.3%
Settled: 2.42 NTU
0 mg/L NaOCl
29 mg/L 961
Filtrate: 0.04 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.38 NTU
1.5 mg/L NaOCl
29 mg/L 961
Filtrate: 0.04 NTU
UVT: 95.7%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 0.95 NTU

## Slide 44: Jars 33-36 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 961

## Slide 45: Jars 33-36: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
0 mg/L NaOCl
29 mg/L 961
Filtrate: 0.03 NTU
UVT: 94.8%
UVA: 0.023/cm
UVA Reduction: 61.7%
Settled: 0.91 NTU
1.5 mg/L NaOCl
29 mg/L 961
Filtrate: 0.03 NTU
UVT: 95.7%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 0.87 NTU
0 mg/L NaOCl
34 mg/L 961
Filtrate: 0.03 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.08 NTU
1.5 mg/L NaOCl
34 mg/L 961
Filtrate: 0.03 NTU
UVT: 96.0%
UVA: 0.017/cm
UVA Reduction: 71.7%
Settled: 0.95 NTU

## Slide 46: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
29 mg/L 961
Filtrate: 0.03 NTU
UVT: 94.8%
UVA: 0.023/cm
UVA Reduction: 61.7%
Settled: 0.91 NTU
1.5 mg/L NaOCl
29 mg/L 961
Filtrate: 0.03 NTU
UVT: 95.7%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 0.87 NTU
0 mg/L NaOCl
34 mg/L 961
Filtrate: 0.03 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.08 NTU
1.5 mg/L NaOCl
34 mg/L 961
Filtrate: 0.03 NTU
UVT: 96.0%
UVA: 0.017/cm
UVA Reduction: 71.7%
Settled: 0.95 NTU

## Slide 47: Jars 37-40 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 905

## Slide 48: Jars 37-40: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
1.5 mg/L NaOCl
5 mg/L 905
Filtrate: 0.06 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction: 55.0%
Settled: 1.09 NTU
1.5 mg/L NaOCl
10 mg/L 905
Filtrate: 0.03 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 1.32 NTU
1.5 mg/L NaOCl
15 mg/L 905
Filtrate: 0.03 NTU
UVT: 96.1%
UVA: 0.017/cm
UVA Reduction: 71.7%
Settled: 1.42 NTU
1.5 mg/L NaOCl
20 mg/L 905
Filtrate: 0.03 NTU
UVT: 96.4%
UVA: 0.015/cm
UVA Reduction: 75.0%
Settled: 1.19 NTU

## Slide 49: Jars 37-40: After 25-minutes of settling, settled water turbidity is taken.
1.5 mg/L NaOCl
5 mg/L 905
Filtrate: 0.06 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction: 55.0%
Settled: 1.09 NTU
1.5 mg/L NaOCl
10 mg/L 905
Filtrate: 0.03 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 1.32 NTU
1.5 mg/L NaOCl
15 mg/L 905
Filtrate: 0.03 NTU
UVT: 96.1%
UVA: 0.017/cm
UVA Reduction: 71.7%
Settled: 1.42 NTU
1.5 mg/L NaOCl
20 mg/L 905
Filtrate: 0.03 NTU
UVT: 96.4%
UVA: 0.015/cm
UVA Reduction: 75.0%
Settled: 1.19 NTU

## Slide 50: Jars 41-44 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 905

## Slide 51: Jars 41-44: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
0 mg/L NaOCl
12 mg/L 905
Filtrate: 0.03 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 1.54 NTU
1.5 mg/L NaOCl
12 mg/L 905
Filtrate: 0.03 NTU
UVT: 95.7%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.80 NTU
0 mg/L NaOCl
15 mg/L 905
Filtrate: 0.08 NTU
UVT: 95.4%
UVA: 0.020/cm
UVA Reduction: 66.7%
Settled: 1.66 NTU
1.5 mg/L NaOCl
15 mg/L 905
Filtrate: 0.04 NTU
UVT: 95.7%
UVA: 0.017/cm
UVA Reduction: 71.7%
Settled: 1.48 NTU

## Slide 52: Jars 41-44: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
12 mg/L 905
Filtrate: 0.03 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 1.54 NTU
1.5 mg/L NaOCl
12 mg/L 905
Filtrate: 0.03 NTU
UVT: 95.7%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.80 NTU
0 mg/L NaOCl
15 mg/L 905
Filtrate: 0.08 NTU
UVT: 95.4%
UVA: 0.020/cm
UVA Reduction: 66.7%
Settled: 1.66 NTU
1.5 mg/L NaOCl
15 mg/L 905
Filtrate: 0.04 NTU
UVT: 95.7%
UVA: 0.017/cm
UVA Reduction: 71.7%
Settled: 1.48 NTU

## Slide 53: Jars 45-48 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 54: Jars 45-48: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
1.5 mg/L NaOCl
6 mg/L 9810
Filtrate: 0.04 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 60.0%
Settled: 1.43 NTU
1.5 mg/L NaOCl
9 mg/L 9810
Filtrate: 0.05 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction: 65.0%
Settled: 1.98 NTU
1.5 mg/L NaOCl
12 mg/L 9810
Filtrate: 0.03 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.72 NTU
1.5 mg/L NaOCl
15 mg/L 9810
Filtrate: 0.03 NTU
UVT: 96.0%
UVA: 0.017/cm
UVA Reduction: 71.7%
Settled: 1.84 NTU

## Slide 55: Jars 45-48: After 25-minutes of settling, settled water turbidity is taken.
1.5 mg/L NaOCl
6 mg/L 9810
Filtrate: 0.04 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 60.0%
Settled: 1.43 NTU
1.5 mg/L NaOCl
9 mg/L 9810
Filtrate: 0.05 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction: 65.0%
Settled: 1.98 NTU
1.5 mg/L NaOCl
12 mg/L 9810
Filtrate: 0.03 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction: 70.0%
Settled: 1.72 NTU
1.5 mg/L NaOCl
15 mg/L 9810
Filtrate: 0.03 NTU
UVT: 96.0%
UVA: 0.017/cm
UVA Reduction: 71.7%
Settled: 1.84 NTU

## Slide 56: Jars 49-52 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 8809, 905, 9810, 961

## Slide 57: Jars 49-52: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.06 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 60.0%
Settled: 1.82 NTU
1.5 mg/L NaOCl
12 mg/L 905
Filtrate: 0.04 NTU
UVT: 95.5%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 2.07 NTU
1.5 mg/L NaOCl
12 mg/L 9810
Filtrate: 0.04 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 1.81 NTU
1.5 mg/L NaOCl
29 mg/L 9810
Filtrate: 0.04 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 0.95 NTU

## Slide 58: Jars 49-52: After 25-minutes of settling, settled water turbidity is taken.
1.5 mg/L NaOCl
6.5 mg/L 8809
Filtrate: 0.06 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 60.0%
Settled: 1.82 NTU
1.5 mg/L NaOCl
12 mg/L 905
Filtrate: 0.04 NTU
UVT: 95.5%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 2.07 NTU
1.5 mg/L NaOCl
12 mg/L 9810
Filtrate: 0.04 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 1.81 NTU
1.5 mg/L NaOCl
29 mg/L 9810
Filtrate: 0.04 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 68.3%
Settled: 0.95 NTU

## Slide 59: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 60: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 61: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 62: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 63: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 64: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732