## Slide 1: Westhaven C.S.D. CA1210024, Humboldt County, Jar Test
by Guy Schott, P.E. October 20, 2020

## Slide 2: Westhaven C.S.D., October 20, 2020 Source Water Characteristics
Source Post Slow-Sand Filtration
pH: 7.20
Turbidity: 0.41 NTU
UVT: 89.9%
UVA: 0.046/cm
0.4 um Filtered
Turbidity: 0.09 NTU
UVT: 89.1%
UVA: 0.050/cm
Using the P200 UVT/UVA analyzer; calibrated with organic free water.

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Applied Coagulants for Jar Testing
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate
45-50% Water
5% polyamine
SG = 1.25-1.34
Max dose: 200 mg/L as product
BWS, Inc.
Advanced Coagulant
AdvFloc-CTC-00011
Polyaluminum Chloride
12.55% Al2O3
64.9% Basicity
SG = 1.299
Max dose: 250 mg/L as product
Gregory F. Nieckarz, Ph.D.
Principal Consultant
SWS Consulting, LLC.
+1.541.953.5112
gregn.swsc@gmail.com

## Slide 5: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
All pH adjusted to 7.5 w/acetic acid solution
LCA #1:
Post Slow-Sand Filtration
pH: 7.20
AdvFloc-CTC-00011:
40.5 mg/L as product
LCA #2:
9810: 6.9 mg/L as product

## Slide 6: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 7: Westhaven CSD: Jar Test 1-8 Results Flash Mix 200 RPM (20 sec); Source: (Post Slow-Sand Filter)
Jar # | 20 RPM Floc Duration minutes | Adv Coag. mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 5 | 30 | 0.08 | 98.1 | 0.008 | 84.0 | 0.69
J2 | 5 | 35 | 0.08 | 98.3 | 0.007 | 86.0 | 0.78
J3 | 5 | 40 | 0.07 | 98.3 | 0.007 | 86.0 | 0.71
J4 | 5 | 45 | 0.07 | 98.3 | 0.007 | 86.0 | 0.37
J5 | 5 | 15 | 0.37 | 90.9 | 0.041 | 18.0 | 0.78
J6 | 5 | 20 | 0.12 | 97.0 | 0.012 | 76.0 | 0.81
J7 | 5 | 25 | 0.08 | 98.2 | 0.007 | 86.0 | 0.89
J8 | 5 | 30 | 0.07 | 98.5 | 0.006 | 88.0 | 0.61

## Slide 8: Westhaven CSD: Jar Test 9-16 Results Flash Mix 200 RPM (20 sec); Source: (Post Slow-Sand Filter)
Jar # | 20 RPM Floc Duration minutes | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 5 | 4.8 | 0.44 | 89.9 | 0.045 | 10.0 | 0.61
J10 | 5 | 5.8 | 0.28 | 94.0 | 0.026 | 48.0 | 0.83
J11 | 5 | 6.8 | 0.37 | 93.5 | 0.029 | 42.0 | 0.95
J12 | 5 | 7.8 | 0.20 | 96.7 | 0.014 | 72.0 | 0.87
J13 | 5 | 9.0 | 0.27 | 96.1 | 0.017 | 66.0 | 0.66
J14 | 5 | 10.2 | 0.10 | 96.7 | 0.015 | 90.0 | 0.64
J15 | 5 | 11.4 | 0.20 | 97.1 | 0.012 | 76.0 | 0.67
J16 | 5 | 12.6 | 0.13 | 97.5 | 0.010 | 80.0 | 0.47

## Slide 9: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant Advanced Coagulant

## Slide 10: Jars 1-4: End of 5-minute flocculation (20 RPM) duration. 25 mL is syringed for filterability and %UVT/UVA.
30 mg/L Adv Coag.
Filtrate 0.08 NTU
UVT: 98.1%
UVA: 0.008/cm
UVA Reduction: 84.0%
Settled: 0.69 NTU
35 mg/L Adv Coag.
Filtrate 0.08 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 86.0%
Settled: 0.78 NTU
40 mg/L Adv Coag.
Filtrate 0.07 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 86.0%
Settled: 0.71 NTU
45 mg/L Adv Coag.
Filtrate 0.07 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 86.0%
Settled: 0.37 NTU

## Slide 11: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
30 mg/L Adv Coag.
Filtrate 0.08 NTU
UVT: 98.1%
UVA: 0.008/cm
UVA Reduction: 84.0%
Settled: 0.69 NTU
35 mg/L Adv Coag.
Filtrate 0.08 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 86.0%
Settled: 0.78 NTU
40 mg/L Adv Coag.
Filtrate 0.07 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 86.0%
Settled: 0.71 NTU
45 mg/L Adv Coag.
Filtrate 0.07 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 86.0%
Settled: 0.37 NTU

## Slide 12: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant Advanced Coagulant

## Slide 13: Jars 5-8: End of 5-minute flocculation (20 RPM) duration. 25 mL is syringed for filterability and %UVT/UVA.
15 mg/L Adv Coag.
Filtrate 0.37 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction: 18.0%
Settled: 0.78 NTU
20 mg/L Adv Coag.
Filtrate 0.12 NTU
UVT: 97.0%
UVA: 0.012/cm
UVA Reduction: 76.0%
Settled: 0.81 NTU
25 mg/L Adv Coag.
Filtrate 0.08 NTU
UVT: 98.2%
UVA: 0.007/cm
UVA Reduction: 86.0%
Settled: 0.89 NTU
30 mg/L Adv Coag.
Filtrate 0.07 NTU
UVT: 98.5%
UVA: 0.006/cm
UVA Reduction: 88.0%
Settled: 0.61 NTU

## Slide 14: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
15 mg/L Adv Coag.
Filtrate 0.37 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction: 18.0%
Settled: 0.78 NTU
20 mg/L Adv Coag.
Filtrate 0.12 NTU
UVT: 97.0%
UVA: 0.012/cm
UVA Reduction: 76.0%
Settled: 0.81 NTU
25 mg/L Adv Coag.
Filtrate 0.08 NTU
UVT: 98.2%
UVA: 0.007/cm
UVA Reduction: 86.0%
Settled: 0.89 NTU
30 mg/L Adv Coag.
Filtrate 0.07 NTU
UVT: 98.5%
UVA: 0.006/cm
UVA Reduction: 88.0%
Settled: 0.61 NTU

## Slide 15: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9810

## Slide 16: Jars 9-12: End of 5-minute flocculation (20 RPM) duration. 25 mL is syringed for filterability and %UVT/UVA.
4.8 mg/L 9810
Filtrate 0.44 NTU
UVT: 89.9%
UVA: 0.045/cm
UVA Reduction: 10.0%
Settled: 0.61 NTU
5.8 mg/L 9810
Filtrate 0.28 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 48.0%
Settled: 0.83 NTU
6.8 mg/L 9810
Filtrate 0.37 NTU
UVT: 93.5%
UVA: 0.029/cm
UVA Reduction: 42.0%
Settled: 0.95 NTU
7.8 mg/L 9810
Filtrate 0.20 NTU
UVT: 96.7%
UVA: 0.014/cm
UVA Reduction: 72.0%
Settled: 0.87 NTU

## Slide 17: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9810

## Slide 18: Jars 13-16: End of 5-minute flocculation (20 RPM) duration. 25 mL is syringed for filterability and %UVT/UVA.
9.0 mg/L 9810
Filtrate 0.27 NTU
UVT: 96.1%
UVA: 0.017/cm
UVA Reduction: 66.0%
Settled: 0.66 NTU
10.2 mg/L 9810
Filtrate 0.10 NTU
UVT: 96.7%
UVA: 0.015/cm
UVA Reduction: 90.0%
Settled: 0.64 NTU
11.4 mg/L 9810
Filtrate 0.20 NTU
UVT: 97.1%
UVA: 0.012/cm
UVA Reduction: 76.0%
Settled: 0.67 NTU
12.6 mg/L 9810
Filtrate 0.13 NTU
UVT: 97.5%
UVA: 0.010/cm
UVA Reduction: 80.0%
Settled: 0.47 NTU

## Slide 19: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
9.0 mg/L 9810
Filtrate 0.27 NTU
UVT: 96.1%
UVA: 0.017/cm
UVA Reduction: 66.0%
Settled: 0.66 NTU
10.2 mg/L 9810
Filtrate 0.10 NTU
UVT: 96.7%
UVA: 0.015/cm
UVA Reduction: 90.0%
Settled: 0.64 NTU
11.4 mg/L 9810
Filtrate 0.20 NTU
UVT: 97.1%
UVA: 0.012/cm
UVA Reduction: 76.0%
Settled: 0.67 NTU
12.6 mg/L 9810
Filtrate 0.13 NTU
UVT: 97.5%
UVA: 0.010/cm
UVA Reduction: 80.0%
Settled: 0.47 NTU

## Slide 20: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate). For this study, 25 mL was taken at end of floc period.
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 21: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 22: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 23: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 24: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 25: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732