## Slide 1: Lazy S Mobile Ranch CA1700609, Lake County, Jar Test
by Guy Schott, P.E. January 20, 2023

## Slide 2: St. Helena Creek/Source

## Slide 3: Lazy S Mobile Ranch Source & Water Characteristics, January 20, 2023
Source – St. Helena Creek
pH: 7.22 -7.48
Alkalinity: 78 mg/L as CaCO3
Turbidity: 4.47 NTU
UVT: 85.0%,
UVA: 0.070/cm
0.4 um Filtered
Turbidity: 0.17 NTU
UVT: 87.7%,
UVA: 0.056/cm

## Slide 4: Applied Coagulants for Jar Testing (1)
Amerfloc 482 (WC1118)
SG = 1.0 – 1.2
pDADMAC (20% active, 80% H2O)
NSF limit: 50 mg/L (product)
Product dose 5 mg/L = 1 mg/L pDADMAC active
BWS, Inc.
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 250 mg/L as Product

## Slide 5: Applied Coagulants for Jar Testing (2)
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product
10 mg/L as 9800 = Reduction 1.18 mg/L as CaCO3

## Slide 6: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 7: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.22-7.48
LCA #1:
Amerfloc 482: 8 mg/L as pDADMAC
Note: overdose (>+80 on LCA)

## Slide 8: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 9: Lazy S Mobile Ranch; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | Amerfloc 482 pDADMAC mg/L | CTC-00011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 2.0 | - | 0.57 | 89.5 | 0.048 | 14.3 | 3.28
J2 | 4.0 | - | 0.45 | 91.8 | 0.037 | 33.9 | 5.92
J3 | 6.0 | - | 1.22 | 92.1 | 0.035 | 37.5 | 7.98
J4 | 8.0 | - | 1.55 | 92.0 | 0.036 | 35.7 | 8.67
J5 | - | 16 | 0.11 | 92.6 | 0.033 | 41.1 | 2.98
J6 | - | 22 | 0.10 | 93.0 | 0.031 | 44.6 | 3.29
J7 | - | 28 | 0.07 | 94.9 | 0.022 | 60.7 | 2.1
J8 | - | 34 | 0.08 | 93.9 | 0.027 | 51.8 | 1.97

## Slide 10: Lazy S Mobile Ranch; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9800 (ACH) mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 4 | 0.64 | 88.7 | 0.051 | 9.0 | 3.53
J10 | 8 | 0.45 | 91.9 | 0.036 | 35.7 | 3.10
J11 | 12 | 0.15 | 95.6 | 0.019 | 66.1 | 3.68
J12 | 16 | 0.05 | 96.7 | 0.014 | 75.0 | 3.75
J13 | 12 | 0.09 | 95.2 | 0.021 | 62.5 | 4.29
J14 | 14 | 0.08 | 95.4 | 0.020 | 64.3 | 4.29
J15 | 16 | 0.05 | 96.0 | 0.017 | 69.6 | 4.08
J16 | 18 | 0.22 | 93.7 | 0.028 | 50.0 | 4.46

## Slide 11: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant Amerfloc 486 (pDADMAC)

## Slide 12: Jars 1-4: End of 5-minute flocculation (20 RPM) duration.
2.0 mg/L pDADMAC
Filtrate: 0.57 NTU
UVT: 89.5%
UVA: 0.048/cm
UVA Reduction: 14.3%
Settled: 3.28 NTU
4.0 mg/L pDADMAC
Filtrate: 0.45 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 33.9%
Settled: 5.92 NTU
6.0 mg/L pDADMAC
Filtrate: 1.22 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 37.5%
Settled: 7.98 NTU
8.0 mg/L pDADMAC
Filtrate: 1.55 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 35.7%
Settled: 8.67 NTU

## Slide 13: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 14: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
2.0 mg/L pDADMAC
Filtrate: 0.57 NTU
UVT: 89.5%
UVA: 0.048/cm
UVA Reduction: 14.3%
Settled: 3.28 NTU
4.0 mg/L pDADMAC
Filtrate: 0.45 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 33.9%
Settled: 5.92 NTU
6.0 mg/L pDADMAC
Filtrate: 1.22 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 37.5%
Settled: 7.98 NTU
8.0 mg/L pDADMAC
Filtrate: 1.55 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 35.7%
Settled: 8.67 NTU

## Slide 15: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant CTC-00011

## Slide 16: Jars 5-8: End of 5-minute flocculation (20 RPM) duration.
16 mg/L CTC-00011
Filtrate: 0.11 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 41.1%
Settled: 2.98 NTU
22 mg/L CTC-00011
Filtrate: 0.10 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction: 44.6%
Settled: 3.29 NTU
28 mg/L CTC-00011
Filtrate: 0.07 NTU
UVT: 94.9%
UVA: 0.022/cm
UVA Reduction: 60.7%
Settled: 2.1 NTU
34 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 92.9%
UVA: 0.027/cm
UVA Reduction: 51.8%
Settled: 1.97 NTU

## Slide 17: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 18: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
16 mg/L CTC-00011
Filtrate: 0.11 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 41.1%
Settled: 2.98 NTU
22 mg/L CTC-00011
Filtrate: 0.10 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction: 44.6%
Settled: 3.29 NTU
28 mg/L CTC-00011
Filtrate: 0.07 NTU
UVT: 94.9%
UVA: 0.022/cm
UVA Reduction: 60.7%
Settled: 2.1 NTU
34 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 92.9%
UVA: 0.027/cm
UVA Reduction: 51.8%
Settled: 1.97 NTU

## Slide 19: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9800 (ACH)

## Slide 20: Jars 9-12: End of 5-minute flocculation (20 RPM) duration.
4 mg/L 9800
Filtrate: 0.64 NTU
UVT: 88.7%
UVA: 0.051/cm
UVA Reduction: 9.0%
Settled: 3.53 NTU
8 mg/L 9800
Filtrate: 0.45 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 35.7%
Settled: 3.10 NTU
12 mg/L 9800
Filtrate: 0.15 NTU
UVT: 95.6%
UVA: 0.019/cm
UVA Reduction: 66.1%
Settled: 3.68 NTU
16 mg/L 9800
Filtrate: 0.05 NTU
UVT: 96.7%
UVA: 0.014/cm
UVA Reduction: 75.0%
Settled: 3.75 NTU

## Slide 21: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9800 (ACH)

## Slide 22: Jars 13-16: End of 5-minute flocculation (20 RPM) duration.
12 mg/L 9800
Filtrate: 0.09 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction: 62.5%
Settled: 4.29 NTU
14 mg/L 9800
Filtrate: 0.08 NTU
UVT: 95.4%
UVA: 0.020/cm
UVA Reduction: 64.3%
Settled: 4.29 NTU
16 mg/L 9800
Filtrate: 0.05 NTU
UVT: 96.0%
UVA: 0.017/cm
UVA Reduction: 69.6%
Settled: 4.08 NTU
18 mg/L 9800
Filtrate: 0.22 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 50.0%
Settled: 4.46 NTU

## Slide 23: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 24: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
12 mg/L 9800
Filtrate: 0.09 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction: 62.5%
Settled: 4.29 NTU
14 mg/L 9800
Filtrate: 0.08 NTU
UVT: 95.4%
UVA: 0.020/cm
UVA Reduction: 64.3%
Settled: 4.29 NTU
16 mg/L 9800
Filtrate: 0.05 NTU
UVT: 96.0%
UVA: 0.017/cm
UVA Reduction: 69.6%
Settled: 4.08 NTU
18 mg/L 9800
Filtrate: 0.22 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 50.0%
Settled: 4.46 NTU

## Slide 25: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 20-30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 26: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 27: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 28: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 29: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 30: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732