## Slide 1: Highlands Mutual Water Company CA1710003 Lake County Jar Test
by Guy Schott, P.E.
January 10, 2019

## Slide 2: Highlands Mutual Water Company Source Water: Clear Lake Conventional Treatment

## Slide 3: Highlands Mutual Water Company, January 10, 2019 Clear Lake Source and Treated Water Characteristics
Source Water Charateristics
Turbidity: 21 NTU
pH: 7.53
UVT: 71.3%, UVA: 0.147/cm
Post Ozone Water Charateristics
Turbidity: 20 NTU
pH: 7.53
UVT: 81.1%, UVA: 0.091/cm
Treatment Plant Operations
9800 Coagulant Dose: 63 mg/L
Settled: 1.4 NTU
Turbidity: 0.04 NTU
UVT: 93.7%
UVA: 0.028/cm

## Slide 4: UVT/UVA
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Coagulant Used for Jar Testing
9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
SG = 1.34

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.53
Source (pre-ozone)
9800: 39.4 mg/L as product
2) Source (pre-ozone)
Added 3.5 mg/L NaOCl
9800: 45.2 mg/L as product
3) Source (post-ozone)
9800: 23.2 mg/L as product
4) Source (post-ozone)
Added 3.5 mg/L NaOCl
9800: 30.7 mg/L as product

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Highlands MWC, Jar Test 1-8 Results (Before-O3 Contactor)
Jar # | 200 RPM Flash Mix Sec | 30 RPM Floc Mix Minutes | NaOCl mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J1 | 60 | 5 | 0 | 18 | 0.11 | 92.5 | 0.034 | 0.85
J2 | 60 | 5 | 0 | 23 | 0.07 | 92.4 | 0.034 | 0.65
J3 | 60 | 5 | 0 | 28 | 0.05 | 93.2 | 0.031 | 0.80
J4 | 60 | 5 | 0 | 33 | 0.09 | 93.1 | 0.031 | 1.0
J5 | 60 | 5 | 0 | 28 | 0.06 | 92.5 | 0.034 | 1.5
J6 | 60 | 5 | 3.5 | 28 | 0.07 | 92.5 | 0.034 | 1.2
J7 | 60 | 5 | 3.5 | 33 | 0.08 | 92.5 | 0.034 | 1.5
J8 | 60 | 5 | 3.5 | 60 | 0.07 | 93.2 | 0.031 | 2.0

## Slide 9: Highlands MWC, Jar Test 9-16 Results (Post O3 Treatment)
Jar # | 200 RPM Flash Mix Sec | 30 RPM Floc Mix Minutes | NaOCl mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J9 | 60 | 5 | 0 | 35 | 0.12 | 87.4 | 0.058 | 0.7
J10 | 60 | 5 | 0 | 40 | 0.08 | 88.2 | 0.055 | 0.65
J11 | 60 | 5 | 0 | 45 | 0.09 | 88.6 | 0.053 | 1.0
J12 | 60 | 5 | 0 | 50 | 0.09 | 88.7 | 0.052 | 1.2
J13 | 60 | 5 | 3.5 | 35 | 0.11 | 88.7 | 0.052 | 0.6
J14 | 60 | 5 | 3.5 | 40 | 0.07 | 88.9 | 0.051 | 0.8
J15 | 60 | 5 | 3.5 | 45 | 0.07 | 89.2 | 0.050 | 0.9
J16 | 60 | 5 | 3.5 | 50 | 0.07 | 89.4 | 0.049 | 0.9

## Slide 10: Jars 1-4 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post Ozone Applied Coagulant 9800

## Slide 11: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
18 mg/L 9800
Filtrate 0.11 NTU
UVT: 92.5%
UVA: 0.034/cm
Settled: 0.85 NTU
23 mg/L 9800
Filtrate 0.07 NTU
UVT: 92.4%
UVA: 0.034/cm
Settled: 0.65 NTU
28 mg/L 9800
Filtrate 0.05 NTU
UVT: 93.2%
UVA: 0.031/cm
Settled: 0.8 NTU
33 mg/L 9800
Filtrate 0.09 NTU
UVT: 93.1%
UVA: 0.031/cm
Settled: 1.0 NTU

## Slide 12: Jars 1-4: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 13: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
18 mg/L 9800
Filtrate 0.11 NTU
UVT: 92.5%
UVA: 0.034/cm
Settled: 0.85 NTU
23 mg/L 9800
Filtrate 0.07 NTU
UVT: 92.4%
UVA: 0.034/cm
Settled: 0.65 NTU
28 mg/L 9800
Filtrate 0.05 NTU
UVT: 93.2%
UVA: 0.031/cm
Settled: 0.8 NTU
33 mg/L 9800
Filtrate 0.09 NTU
UVT: 93.1%
UVA: 0.031/cm
Settled: 1.0 NTU

## Slide 14: Jars 5-8 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post Ozone Applied Coagulant 9800 w/NaOCl

## Slide 15: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
3.5 mg/L NaOCl
28 mg/L 9800
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.034/cm
Settled: 1.2 NTU
3.5 mg/L NaOCl
33 mg/L 9800
Filtrate 0.08 NTU
UVT: 92.5%
UVA: 0.034/cm
Settled: 1.5 NTU
3.5 mg/L NaOCl
60 mg/L 9800
Filtrate 0.07 NTU
UVT: 93.2%
UVA: 0.031/cm
Settled: 2.0 NTU
0 mg/L NaOCl
28 mg/L 9800
Filtrate 0.06 NTU
UVT: 92.5%
UVA: 0.034/cm
Settled: 1.5 NTU

## Slide 16: Jars 5-8: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 17: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
28 mg/L 9800
Filtrate 0.06 NTU
UVT: 92.5%
UVA: 0.034/cm
Settled: 1.5 NTU
3.5 mg/L NaOCl
28 mg/L 9800
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.034/cm
Settled: 1.2 NTU
3.5 mg/L NaOCl
33 mg/L 9800
Filtrate 0.08 NTU
UVT: 92.5%
UVA: 0.034/cm
Settled: 1.5 NTU
3.5 mg/L NaOCl
60 mg/L 9800
Filtrate 0.07 NTU
UVT: 93.2%
UVA: 0.031/cm
Settled: 2.0 NTU

## Slide 18: Jars 9-12 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Pre Ozone Applied Coagulant 9800

## Slide 19: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
35 mg/L 9800
Filtrate 0.12 NTU
UVT: 87.4%
UVA: 0.058/cm
Settled: 0.7 NTU
40 mg/L 9800
Filtrate 0.08 NTU
UVT: 88.2%
UVA: 0.055/cm
Settled: 0.65 NTU
45 mg/L 9800
Filtrate 0.09 NTU
UVT: 88.6%
UVA: 0.053/cm
Settled: 1.0 NTU
50 mg/L 9800
Filtrate 0.09 NTU
UVT: 88.7%
UVA: 0.052/cm
Settled: 1.2 NTU

## Slide 20: Jars 9-12: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 21: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.

## Slide 22: Jars 13-16 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Pre Ozone Applied Coagulant 9800 w/NaOCl

## Slide 23: Jars 13-6: End of 5-minute flocculation (30 RPM) duration.
3.5 mg/L NaOCl
35 mg/L 9800
Filtrate 0.11 NTU
UVT: 88.7%
UVA: 0.052/cm
Settled: 0.6 NTU
3.5 mg/L NaOCl
40 mg/L 9800
Filtrate 0.07 NTU
UVT: 88.9%
UVA: 0.051/cm
Settled: 0.8 NTU
3.5 mg/L NaOCl
45 mg/L 9800
Filtrate 0.07 NTU
UVT: 89.2%
UVA: 0.050/cm
Settled: 0.9 NTU
3.5 mg/L NaOCl
50 mg/L 9800
Filtrate 0.07 NTU
UVT: 89.4%
UVA: 0.049/cm
Settled: 0.9 NTU

## Slide 24: Jars 13-16: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 25: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.

## Slide 26: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 27: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 28: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 29: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 30: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 31: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732