## Slide 1: Konocti Harbor Resort & Spa CA1710016 Lake County Jar Test
by Guy Schott, P.E.
April 20, 2020

## Slide 2: Konocti Harbor Resort & Spa Source Water Characteristics April 20, 2020
Source
Turbidity: 2.75 NTU
pH: 8.14
UVT: 85.9%, UVA: 0.065/cm
0.4 um Filtered
Turbidity: 0.25 NTU
UVT: 88.1%, UVA: 0.054/cm

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Coagulant Used for Jar Testing
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate (ACH)
45-50% Water
5% Proprietary
SG = 1.25 – 1.34
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate (ACH)
35-45% Water
20% Proprietary
SG = 1.25 – 1.34

## Slide 5: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 8.14
LCA #1:
9810: 14 mg/L as product
pH adjusted to 7.5 with Acetic Acid
LCA #2:
9890: 12 mg/L as product
pH adjusted to 7.5 with Acetic Acid

## Slide 6: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 7: Konocti Harbor Resort Spa, Source: Clear Lake Jar Test 1-8 Results, Flash Mix 200 RPM (15 sec)
Jar # | 20 RPM Floc Mix (minutes) | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 5 | 12 | 0.16 | 91.0 | 0.049 | 25.9 | 1.10
J2 | 5 | 14 | 0.13 | 91.3 | 0.039 | 27.8 | 1.01
J3 | 5 | 16 | 0.09 | 91.7 | 0.037 | 31.5 | 0.94
J4 | 5 | 18 | 0.09 | 91.8 | 0.036 | 33.3 | 0.67
J5 | 5 | 20 | 0.09 | 92.2 | 0.035 | 35.2 | 0.74
J6 | 5 | 22 | 0.07 | 92.4 | 0.034 | 37.0 | 0.57
J7 | 5 | 24 | 0.07 | 92.4 | 0.034 | 37.0 | 0.60
J8 | 5 | 26 | 0.07 | 92.6 | 0.033 | 38.9 | 0.56

## Slide 8: Konocti Harbor Resort Spa, Source: Clear Lake Jar Test 9-16 Results, Flash Mix 200 RPM (15 sec)
Jar # | 20 RPM Floc Mix (minutes) | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 5 | 12 | 0.18 | 91.2 | 0.039 | 27.8 | 1.14
J10 | 5 | 14 | 0.26 | 91.2 | 0.039 | 27.8 | 1.15
J11 | 5 | 16 | 0.34 | 91.2 | 0.039 | 27.8 | 1.12
J12 | 5 | 18 | 0.16 | 91.4 | 0.039 | 27.8 | 0.90
J13 | 5 | 20 | 0.08 | 92.3 | 0.034 | 37.0 | 1.0
J14 | 5 | 22 | 0.07 | 92.5 | 0.033 | 38.9 | 1.02
J15 | 5 | 24 | 0.07 | 92.5 | 0.033 | 38.9 | 0.97
J16 | 5 | 26 | 0.12 | 92.5 | 0.033 | 38.9 | 0.90

## Slide 9: Konocti Harbor Resort Spa, Source: Clear Lake Jar Test 17-24 Results, Flash Mix 200 RPM (15 sec)
Jar # | 20 RPM Floc Mix (min) | 9810 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 20 | 22 | 0 | 0.08 | 92.8 | 0.032 | 40.7 | 0.72
J18 | 20 | 0 | 22 | 0.09 | 92.6 | 0.033 | 38.9 | 0.97
J19 | 20 | 26 | 0 | 0.07 | 92.6 | 0.033 | 38.9 | 0.55
J20 | 20 | 0 | 26 | 0.08 | 92.6 | 0.033 | 38.9 | 0.85
J21 | 30 | 22 | 0 | 0.09 | 92.6 | 0.033 | 38.9 | 0.40
J22 | 30 | 0 | 22 | 0.12 | 92.4 | 0.034 | 37.0 | 0.60
J23 | 30 | 26 | 0 | 0.09 | 92.6 | 0.033 | 38.9 | 0.64
J24 | 30 | 0 | 26 | 0.09 | 92.4 | 0.034 | 37.0 | 0.66

## Slide 10: Jars 1-4 Test Flash Mix 15 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9810

## Slide 11: Jars 1-4: End of 5-minute flocculation (20 RPM) duration.
14 mg/L 9810
Filtrate 0.13 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 27.8%
Settled: 1.01 NTU
12 mg/L 9810
Filtrate 0.16 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 25.9%
Settled: 1.10 NTU
16 mg/L 9810
Filtrate 0.09 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 31.5%
Settled: 0.94 NTU
18 mg/L 9810
Filtrate 0.09 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction 33.3%
Settled: 0.67 NTU

## Slide 12: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 13: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
14 mg/L 9810
Filtrate 0.13 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 27.8%
Settled: 1.01 NTU
12 mg/L 9810
Filtrate 0.16 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 25.9%
Settled: 1.10 NTU
16 mg/L 9810
Filtrate 0.09 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 31.5%
Settled: 0.94 NTU
18 mg/L 9810
Filtrate 0.09 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction 33.3%
Settled: 0.67 NTU

## Slide 14: Jars 5-8 Test Flash Mix 15 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9810

## Slide 15: Jars 5-8: End of 5-minute flocculation (20 RPM) duration.
20 mg/L 9810
Filtrate 0.09 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 35.2%
Settled: 0.74 NTU
22 mg/L 9810
Filtrate 0.07 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 0.57 NTU
24 mg/L 9810
Filtrate 0.07 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 0.60 NTU
26 mg/L 9810
Filtrate 0.07 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.56 NTU

## Slide 16: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 17: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L 9810
Filtrate 0.09 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 35.2%
Settled: 0.74 NTU
22 mg/L 9810
Filtrate 0.07 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 0.57 NTU
24 mg/L 9810
Filtrate 0.07 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 0.60 NTU
26 mg/L 9810
Filtrate 0.07 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.56 NTU

## Slide 18: Jars 9-12 Test Flash Mix 15 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9890

## Slide 19: Jars 9-12: End of 5-minute flocculation (20 RPM) duration.
12 mg/L 9890
Filtrate 0.18 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 27.8%
Settled: 1.14 NTU
14 mg/L 9890
Filtrate 0.23 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 37%
Settled: 1.15 NTU
16 mg/L 9890
Filtrate 0.34 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 37%
Settled: 1.12 NTU
18 mg/L 9890
Filtrate 0.34 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 37%
Settled: 0.90 NTU

## Slide 20: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 21: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
12 mg/L 9890
Filtrate 0.18 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 27.8%
Settled: 1.14 NTU
14 mg/L 9890
Filtrate 0.23 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 37%
Settled: 1.15 NTU
16 mg/L 9890
Filtrate 0.34 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 37%
Settled: 1.12 NTU
18 mg/L 9890
Filtrate 0.34 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 37%
Settled: 0.90 NTU

## Slide 22: Jars 13-16 Test Flash Mix 15 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulant 9890

## Slide 23: Jars 13-16: End of 5-minute flocculation (20 RPM) duration.
20 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 1.0 NTU
22 mg/L 9890
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 1.02 NTU
24 mg/L 9890
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.97 NTU
26 mg/L 9890
Filtrate 0.12 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.90 NTU

## Slide 24: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 1.0 NTU
22 mg/L 9890
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 1.02 NTU
24 mg/L 9890
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.97 NTU
26 mg/L 9890
Filtrate 0.12 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.90 NTU

## Slide 25: Jars 17-20 Test Flash Mix 15 Sec (200 RPM) Floc Mix 5 min (20 RPM) Applied Coagulants 9810 9890

## Slide 26: Jars 17-20: End of 5-minute flocculation (20 RPM) duration.
22 mg/L 9810
Filtrate 0.08 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction 40.7%
Settled: 0.72 NTU
22 mg/L 9890
Filtrate 0.09 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.97 NTU
26 mg/L 9810
Filtrate 0.07 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.55 NTU
26 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.85 NTU

## Slide 27: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 28: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
22 mg/L 9810
Filtrate 0.08 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction 40.7%
Settled: 0.72 NTU
22 mg/L 9890
Filtrate 0.09 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.97 NTU
26 mg/L 9810
Filtrate 0.07 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.55 NTU
26 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.85 NTU

## Slide 29: Jars 21-24 Test Flash Mix 15 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9810 9890

## Slide 30: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
22 mg/L 9810
Filtrate 0.09 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.40 NTU
22 mg/L 9890
Filtrate 0.12 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 0.60 NTU
26 mg/L 9810
Filtrate 0.09 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.64 NTU
26 mg/L 9890
Filtrate 0.09 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 0.66 NTU

## Slide 31: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 32: Jars 21-24: After 25-minutes of settling, settled water turbidity is sampled.
22 mg/L 9810
Filtrate 0.09 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.40 NTU
22 mg/L 9890
Filtrate 0.12 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 0.60 NTU
26 mg/L 9810
Filtrate 0.09 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 38.9%
Settled: 0.64 NTU
26 mg/L 9890
Filtrate 0.09 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 37%
Settled: 0.66 NTU

## Slide 33: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 34: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 35: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 36: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 37: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 38: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732