## Slide 1: Lake County CSA 21, North Lakeport CA1710021, Lake County Jar Test
by Guy Schott, P.E.
November 10, 2022

## Slide 2: Lake County CSA 21, North Lakeport Trident Surface Water Facility
Pre-Ozone
Tower
Clearwell

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: North Lakeport Source Water Characteristics, November 10, 2022
Plant Coagulant Dose:
Pro Pac 9890: 11.8 mg/L
Zeta Floc PA 50: 3.8 mg/L (polyamine solution)
Source – Before Ozone Injection
pH: 8.46
Alkalinity: 202 mg/L as CaCO3
Turbidity: 61 NTU
UVT: 59.3%,
UVA: 0.226/cm
0.4 um Filtered
Turbidity: 0.42 NTU
UVT: 81.4%,
UVA: 0.089/cm
Plant Filtrate Water
pH: 8.50
Alkalinity: 197 mg/L as CaCO3
Turbidity: 0.12 NTU
UVT: 88.7%,
UVA: 0.051/cm
Plant Filtrate GAC Water
pH: 8.63
Alkalinity: 199 mg/L as CaCO3
Turbidity: 0.07 NTU
UVT: 91.7%,
UVA: 0.039/cm
Note: Jar testing results are based on source water characteristic,
without applied ozone.

## Slide 5: Applied Coagulants for Jar Testing (1)
Pro Pac 9890, NTU Technologies
35-45% Aluminum Chlorohydrate
20% polyamine solution (50% water, 50% active polyamine)
35-45% Water
~18.9% Al2O3
~10.5% Al
83% Basicity
SG = 1.25-1.34
NSF Max Use: 50 mg/L as Product;
Product dose 50 mg/L = 5 mg/L polyamine active
Zeta Floc PA 50, NTU Technologies
Polyamine (PY)
NSF Max Use: 10 mg/L as Product
(50% water, 50% active polyamine)
Product dose 10 mg/L = 5 mg/L polyamine active

## Slide 6: Applied Coagulants for Jar Testing (2)
Pro Pac 9810, NTU Technologies
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine solution (50% water, 50% active polyamine)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 200 mg/L = 5 mg/L active polyamine

## Slide 7: Polyamine C59H108N14O10 MW: 1,173.6 g/mol

## Slide 8: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 8.46 (post Ozone)
LCA #1: Manually add Zeta Floc PA 50, 4 mg/L
Pro Pac 9890: 8.6 mg/L
pH adjusted to 7.8 with acetic acid
LCA #2: 9810: Pro Pac 9890: 35.6 mg/L
pH adjusted to 7.8 with acetic acid
LCA #3: 9810: 60.5 mg/L
pH adjusted to 7.8 with acetic acid

## Slide 9: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 10: CSA 21 North Lakeport; Clear Lake; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Pro Pac 9890 mg/L | Zeta Floc PA 50 Polyamine | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J1 | 16 | 0 | 0.30 | 84.5 | 0.073 | 18.0
J2 | 35 | 0 | 0.13 | 85.6 | 0.067 | 24.7
J3 | 40 | 0 | 0.09 | 86.9 | 0.060 | 32.6
J4 | 45 | 0 | 0.09 | 86.4 | 0.063 | 29.2
J5 | 16 | 1 | 0.17 | 84.7 | 0.072 | 19.1
J6 | 16 | 2 | 0.14 | 85.1 | 0.069 | 22.5
J7 | 16 | 3 | 0.10 | 85.8 | 0.066 | 25.8
J8 | 16 | 4 | 0.11 | 85.6 | 0.067 | 24.7

## Slide 11: CSA 21 North Lakeport; Clear Lake; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Pro Pac 9810 mg/L | Zeta Floc PA 50 Polyamine | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J9 | 55 | 0 | 0.07 | 86.4 | 0.063 | 29.2
J10 | 60 | 0 | 0.08 | 86.6 | 0.062 | 30.3
J11 | 65 | 0 | 0.08 | 86.8 | 0.061 | 31.5
J12 | 70 | 0 | 0.10 | 86.9 | 0.060 | 32.6
J13 | 55 | 3 | 0.06 | 87.3 | 0.059 | 33.7
J14 | 60 | 3 | 0.08 | 87.3 | 0.058 | 34.8
J15 | 65 | 3 | 0.06 | 87.7 | 0.057 | 36.0
J16 | 70 | 3 | 0.06 | 87.8 | 0.056 | 37.1

## Slide 12: CSA 21 North Lakeport; Clear Lake; Jar Test 17 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Pro Pac 9890 mg/L | Pro Pac 9810 mg/L | Zeta Floc PA 50 Polyamine | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J17 | 20 | - | 3 | 0.12 | 85.8 | 0.066 | 25.8
J18 | 25 | - | 3 | 0.10 | 86.0 | 0.065 | 27.0
J19 | 30 | - | 3 | 0.08 | 86.1 | 0.064 | 28.1
J20 | 35 | - | 3 | 0.09 | 86.4 | 0.063 | 29.2
J21 | - | 70 | 3 | 0.06 | 88.0 | 0.055 | 38.2
J22 | - | 80 | 3 | 0.05 | 88.2 | 0.054 | 39.3
J23 | - | 90 | 3 | 0.05 | 89.0 | 0.050 | 43.8
J24 | - | 100 | 3 | 0.05 | 88.5 | 0.052 | 41.6

## Slide 13: CSA 21 North Lakeport; Clear Lake; Jar Test 25 - 28 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Pro Pac 9890 mg/L | Pro Pac 9810 mg/L | Zeta Floc PA 50 Polyamine | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J25 | 12 | - | 4 | 0.16 | 85.5 | 0.067 | 24.7
J26 | 35 | - | 4 | 0.08 | 86.0 | 0.065 | 27.0
J27 | - | 90 | 0 | 0.08 | 87.1 | 0.059 | 33.7
J28 | - | 90 | 3 | 0.06 | 88.9 | 0.050 | 43.8

## Slide 14: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Without-Ozone Applied Coagulant Pro Pac 9890

## Slide 15: Jars 1-4: During Flocculation

## Slide 16: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
16 mg/L 9890
Filtrate 0.30 NTU
UVT: 84.5%
UVA: 0.073/cm
UVA Reduction: 18.0%
35 mg/L 9890
Filtrate 0.13 NTU
UVT: 85.6%
UVA: 0.067/cm
UVA Reduction: 24.7%
40 mg/L 9890
Filtrate 0.09 NTU
UVT: 86.9%
UVA: 0.060/cm
UVA Reduction: 32.6%
45 mg/L 9890
Filtrate 0.09 NTU
UVT: 86.4%
UVA: 0.063/cm
UVA Reduction: 29.2%

## Slide 17: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Without-Ozone Applied Coagulants Pro Pac 9890 Zeta Floc PA 50

## Slide 18: Jars 5-8: During Flocculation

## Slide 19: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
16 mg/L 9890
1 mg/L Zeta Floc PA 50
Filtrate 0.17 NTU
UVT: 84.7%
UVA: 0.072/cm
UVA Reduction: 19.1%
16 mg/L 9890
2 mg/L Zeta Floc PA 50
Filtrate 0.14 NTU
UVT: 85.1%
UVA: 0.069/cm
UVA Reduction: 22.5%
16 mg/L 9890
3 mg/L Zeta Floc PA 50
Filtrate 0.10 NTU
UVT: 85.8%
UVA: 0.066/cm
UVA Reduction: 25.8%
16 mg/L 9890
4 mg/L Zeta Floc PA 50
Filtrate 0.11 NTU
UVT: 85.6%
UVA: 0.067cm
UVA Reduction: 24.7%

## Slide 20: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Without-Ozone Applied Coagulant Pro Pac 9810

## Slide 21: Jars 9-12: During Flocculation

## Slide 22: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
55 mg/L 9810
Filtrate 0.07 NTU
UVT: 86.4%
UVA: 0.073/cm
UVA Reduction: 29.2%
60 mg/L 9810
Filtrate 0.08 NTU
UVT: 86.6%
UVA: 0.067/cm
UVA Reduction: 30.3%
65 mg/L 9810
Filtrate 0.08 NTU
UVT: 86.8%
UVA: 0.060/cm
UVA Reduction: 31.5%
70 mg/L 9810
Filtrate 0.10 NTU
UVT: 86.9%
UVA: 0.063/cm
UVA Reduction: 32.6%

## Slide 23: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Without-Ozone Applied Coagulants Pro Pac 9810 Zeta Floc PA 50

## Slide 24: Jars 13-16: During Flocculation

## Slide 25: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
55 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.06 NTU
UVT: 87.3%
UVA: 0.059/cm
UVA Reduction: 33.7%
60 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.08 NTU
UVT: 87.3%
UVA: 0.058/cm
UVA Reduction: 34.8%
65 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.06 NTU
UVT: 87.7%
UVA: 0.057/cm
UVA Reduction: 36.0%
70 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.06 NTU
UVT: 87.8%
UVA: 0.057cm
UVA Reduction: 37.1%

## Slide 26: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Without-Ozone Applied Coagulants Pro Pac 9890 Zeta Floc PA 50

## Slide 27: Jars 17-20: During Flocculation

## Slide 28: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
20 mg/L 9890
3 mg/L Zeta Floc PA 50
Filtrate 0.12 NTU
UVT: 85.8%
UVA: 0.066/cm
UVA Reduction: 25.8%
25 mg/L 9890
3 mg/L Zeta Floc PA 50
Filtrate 0.10 NTU
UVT: 86.0%
UVA: 0.065/cm
UVA Reduction: 27.0%
30 mg/L 9890
3 mg/L Zeta Floc PA 50
Filtrate 0.08 NTU
UVT: 86.1%
UVA: 0.064/cm
UVA Reduction: 28.1%
35 mg/L 9890
3 mg/L Zeta Floc PA 50
Filtrate 0.09 NTU
UVT: 86.4%
UVA: 0.063cm
UVA Reduction: 29.2%

## Slide 29: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Without-Ozone Applied Coagulant 9810

## Slide 30: Jars 21-24: During Flocculation

## Slide 31: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
70 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.06 NTU
UVT: 88.0%
UVA: 0.055/cm
UVA Reduction: 38.2%
80 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.05 NTU
UVT: 88.2%
UVA: 0.054/cm
UVA Reduction: 39.3%
90 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.05 NTU
UVT: 89.0%
UVA: 0.050/cm
UVA Reduction: 43.8%
100 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.05 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction: 41.6%

## Slide 32: Jars 25-28 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Without-Ozone Applied Coagulants Pro Pac 9890 Pro Pac 9810 Zeta Floc PA 50

## Slide 33: Jars 25-28: During Flocculation

## Slide 34: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
12 mg/L 9890
4 mg/L Zeta Floc PA 50
Filtrate 0.16 NTU
UVT: 85.5%
UVA: 0.067/cm
UVA Reduction: 24.7%
80 mg/L 9890
4 mg/L Zeta Floc PA 50
Filtrate 0.08 NTU
UVT: 86.0%
UVA: 0.065/cm
UVA Reduction: 27.0%
90 mg/L 9810
0 mg/L Zeta Floc PA 50
Filtrate 0.08 NTU
UVT: 87.1%
UVA: 0.059/cm
UVA Reduction: 33.7%
90 mg/L 9810
3 mg/L Zeta Floc PA 50
Filtrate 0.06 NTU
UVT: 88.9%
UVA: 0.050/cm
UVA Reduction: 43.8%

## Slide 35: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 36: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 37: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 38: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 39: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 40: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Jar Test Results/Procedures for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right video training https://youtu.be/aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732