## Slide 1: Surfwood Mutual Water Corporation CA2300590 Mendocino County Jar Test
by Guy Schott, P.E
April 29, 2020

## Slide 2: Source Water: Jack Peter’s Creek Roughing Filter followed by Multi-Media Filtration
Source Water Characteristics
Turbidity: 2.57 NTU
pH: 7.12
UVT: 78.6%
UVA: 0.104/cm
0.6 um Filtered
Turbidity: 0.15 NTU
UVT: 93.0%
UVA: 0.031/cm

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Coagulant Used for Jar Testing
Advanced Coagulant
SG = 1.3
7066 (Garratt Callahan)
10 – 30% Poly Aluminum Hydroxychloride Sulfate
SG = 1.2

## Slide 5: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.12
LCA #1:
7066: 22.5 mg/L as product (no pH adjustment)
Final pH: 6.93
LCA #2:
Advanced Coagulant: 19 mg/L as product
(no pH adjustment)
Final pH: 6.95

## Slide 6: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 7: Filtrate and %UVT/UVA Analysis
For this study, all jars were samples for Filtrate and %UVT/UVA analysis immediately at the end of the flocculation period.

## Slide 8: Surfwood MWC: Jar Test 1-4 Results
Jar # | 200 RPM Flash Mix sec | 30 RPM Floc Duration min | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 30 | 5 | 22.5 | 0.07 | 96.5 | 0.015 | 51.6 | 0.68
J2 | 30 | 5 | 25 | 0.07 | 96.4 | 0.015 | 51.6 | 0.75
J3 | 30 | 5 | 27.5 | 0.08 | 96.5 | 0.015 | 51.6 | 0.84
J4 | 30 | 5 | 30 | 0.08 | 96.6 | 0.014 | 54.8 | 0.75

## Slide 9: Surfwood MWC: Jar Test 5-8 Results
Jar # | 200 RPM Flash Mix sec | 30 RPM Floc Duration min | Adv Coag mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J5 | 30 | 5 | 19 | 0.14 | 96.3 | 0.016 | 51.6 | 0.60
J6 | 30 | 5 | 21 | 0.09 | 96.1 | 0.017 | 45.2 | 0.71
J7 | 30 | 5 | 23 | 0.08 | 96.2 | 0.016 | 48.4 | 0.82
J8 | 30 | 5 | 25 | 0.07 | 96.5 | 0.015 | 51.6 | 0.68

## Slide 10: Surfwood MWC: Jar Test 9-12 Results Flash Mix 200 RPM (30 sec)
Jar #54. | 30 RPM Floc Duration Minutes | 7066 mg/L | Adv Coag mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 5 | 0 | 25 | 0.08 | 96.4 | 0.015 | 51.6 | 0.53
J10 | 5 | 0 | 27 | 0.08 | 96.5 | 0.015 | 51.6 | 0.67
J11 | 5 | 22.5 | 0 | 0.08 | 96.0 | 0.017 | 45.2 | 0.70
J12 | 5 | 32.5 | 0 | 0.06 | 96.7 | 0.014 | 54.8 | 0.70

## Slide 11: Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 12: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
22.5 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.5%
UVA: 0.015/cm
UVA Reduction 51.6%
Settled: 0.68 NTU
25 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.4%
UVA: 0.015/cm
UVA Reduction 51.6%
Settled: 0.75 NTU
27.5 mg/L 7066
Filtrate 0.08 NTU
UVT: 96.5%
UVA: 0.015/cm
UVA Reduction 51.6%
Settled: 0.84 NTU
30 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.6%
UVA: 0.014/cm
UVA Reduction 54.8%
Settled: 0.75 NTU

## Slide 13: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.

## Slide 14: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant Adv Coag

## Slide 15: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
19 mg/L Adv Coag
Filtrate 0.14 NTU
UVT: 96.3%
UVA: 0.016/cm
UVA Reduction 51.6%
Settled: 0.60 NTU
21 mg/L Adv Coag
Filtrate 0.09 NTU
UVT: 96.1%
UVA: 0.017/cm
UVA Reduction 45.2%
Settled: 0.71 NTU
23 mg/L Adv Coag
Filtrate 0.08 NTU
UVT: 96.2%
UVA: 0.016/cm
UVA Reduction 48.4%
Settled: 0.82 NTU
25 mg/L Adv Coag
Filtrate 0.07 NTU
UVT: 96.5%
UVA: 0.015/cm
UVA Reduction 51.6%
Settled: 0.68 NTU

## Slide 16: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.

## Slide 17: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulants 7066/Adv Coag

## Slide 18: Jars 9-12: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
25 mg/L Adv Coag
Filtrate 0.08 NTU
UVT: 96.4%
UVA: 0.015/cm
UVA Reduction 51.6%
Settled: 0.53 NTU
27 mg/L Adv Coag
Filtrate 0.08 NTU
UVT: 96.5%
UVA: 0.015/cm
UVA Reduction 51.6%
Settled: 0.67 NTU
22.5 mg/L 7066
Filtrate 0.08 NTU
UVT: 96.0%
UVA: 0.017/cm
UVA Reduction 45.2%
Settled: 0.70 NTU
32.5 mg/L 7066
Filtrate 0.06 NTU
UVT: 96.7%
UVA: 0.014/cm
UVA Reduction 54.8%
Settled: 0.70 NTU

## Slide 19: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.

## Slide 20: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate). For this study, sample was taken immediately at the end of flocculation process.
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 21: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 22: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 23: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 24: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 25: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732