## Slide 1: Westport County Water District CA2300730 Mendocino County Jar Test
by Guy Schott, P.E
August 21, 2023

## Slide 2: Source Water: Wage Creek - Direct Filtration August 21, 2023
Source – Wage Creek
pH: 7.10
Alkalinity: 77 mg/L as CaCO3
Turbidity: 1.0 NTU
UVT: 93.0%,
UVA: 0.031/cm
0.4 um Filtered
Turbidity: 0.29 NTU
UVT: 94.6%,
UVA: 0.023/cm

## Slide 3: Westport CWS Source Particle Counts August 21, 2023
Particle Size Range (um) | Number of Particles per mL
2-3 | 1,017
3-5 | 580
5-7 | 206
7-10 | 44
10-15 | 13
15-25 | 6
25-50 | 2
>50 | 0
Total: | 1,864

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Applied Coagulants for Jar Testing (1)
960 (NTU Technologies)
33% Polyaluminum Hydroxychlorosulfate
67% Water
SG = 1.29
NSF limit: 250 mg/L as Product
961 (NTU Technologies)
~32% Polyaluminum Hydroxychlorosulfate
66% Water
2% pDADMAC
Active pDADMAC: 0.02 x 255 = 5.1 mg/L
SG = 1.29
NSF limit: 255 mg/L as Product

## Slide 6: Applied Coagulants for Jar Testing (2)
NTU Technologies
Pro Pac 9810
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
Active polyamine: 0.05 x 0.5 x 200 = 5 mg/L
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 20 mg/L = 0.5 mg/L polyamines active
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product
926 (NTU Technologies)
35% Aluminum Chlorohydrate
35% Water
30% pDADMAC (60% H2O, 40% pDADMAC active)
Active pDADMAC: 0.3 x 0.4 x 83 = 10 mg/L
SG = 1.2 – 1.34
NSF limit: 83 mg/L as Product

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 2.0, 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Filtrate and %UVT/UVA Analysis
For this study, all jars were samples for Filtrate and %UVT/UVA analysis immediately at the end of the flocculation period.

## Slide 9: Westport CWS; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J1 | 2.5 | 0.20 | 97.1 | 0.012 | 47.8
J2 | 3.0 | 0.31 | 96.6 | 0.014 | 39.1
J3 | 3.5 | 0.15 | 97.4 | 0.011 | 52.2
J4 | 4.0 | 0.05 | 98.0 | 0.008 | 65.2
J5 | 4.0 | 0.06 | 98.3 | 0.007 | 69.6
J6 | 4.5 | 0.07 | 98.3 | 0.007 | 69.6
J7 | 5.0 | 0.07 | 98.4 | 0.007 | 69.6
J8 | 5.5 | 0.17 | 98.0 | 0.008 | 65.2

## Slide 10: Westport CWS; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | NaOCl mg/L | 960 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Cl2 mg/L
J9 | 0 | 12 | 0.04 | 98.1 | 0.008 | 65.2 | -
J10 | 0 | 16 | 0.10 | 98.0 | 0.008 | 65.2 | -
J11 | 0 | 20 | 0.04 | 98.6 | 0.006 | 73.9 | -
J12 | 0 | 24 | 0.03 | 98.6 | 0.006 | 73.9 | -
J13 | 0 | 20 | 0.04 | 98.6 | 0.006 | 73.9 | -
J14 | 3.0 | 20 | 0.12 | 97.7 | 0.010 | 56.5 | 2.12
J15 | 4.0 | 20 | 0.09 | 97.7 | 0.010 | 56.5 | >2.2
J16 | 5.0 | 20 | 0.03 | 97.8 | 0.009 | 60.9 | >2.2

## Slide 11: Westport CWS; Jar Test 17 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | NaOCl mg/L | 961 mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Cl2 mg/L
J17 | 0 | 16 | - | 0.03 | 98.2 | 0.007 | 69.6 | -
J18 | 2.5 | 16 | - | 0.04 | 97.9 | 0.009 | 60.9 | 1.95
J19 | 0 | 20 | - | 0.05 | 98.1 | 0.008 | 65.2 | -
J20 | 2.5 | 20 | - | 0.06 | 97.6 | 0.010 | 56.5 | 1.73
J21 | 0 | - | 3.6 | 0.21 | 97.3 | 0.011 | 52.2 | -
J22 | 2.5 | - | 3.6 | 0.03 | 98.0 | 0.008 | 65.2 | 1.96
J23 | 0 | - | 4.0 | 0.03 | 98.3 | 0.007 | 69.6 | -
J24 | 2.5 | - | 4.0 | 0.04 | 98.0 | 0.008 | 65.2 | 1.95

## Slide 12: Westport CWS; Jar Test 25 - 32 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | NaOCl mg/L | 926 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Cl2 mg/L
J25 | - | 3.0 | - | 0.03 | 98.3 | 0.007 | 69.6 | -
J26 | - | 3.6 | - | 0.12 | 97.9 | 0.009 | 60.9 | -
J27 | - | - | 3.0 | 0.13 | 97.5 | 0.010 | 56.5 | -
J28 | - | - | 3.6 | 0.36 | 95.8 | 0.018 | 21.7 | -
J29 | 0 | 2.6 | - | 0.14 | 97.7 | 0.010 | 56.5 | -
J30 | 2.5 | 2.6 | - | 0.09 | 97.5 | 0.010 | 56.5 | 1.99
J31 | 0 | 3.0 | - | 0.05 | 98.3 | 0.007 | 69.6 | -
J32 | 2.5 | 3.0 | - | 0.04 | 98.1 | 0.008 | 65.2 | 1.98

## Slide 13: Westport CWS; Jar Test 33 - 35 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | NaOCl mg/L | 926 mg/L | 9910 mg/L | 961 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Cl2 mg/L
J33 | 2.5 | 3.0 | - | - | 0.16 | 97.0 | 0.013 | 43.5 | 1.98
J34 | 2.5 | - | 4.0 | - | 0.23 | 96.3 | 0.016 | 30.4 | 1.96
J35 | 2.5 | - | - | 20 | 0.03 | 97.9 | 0.009 | 60.9 | 1.90

## Slide 14: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 9800

## Slide 15: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
2.5 mg/L 9800
Filtrate: 0.20 NTU
UVT: 97.1%
UVA: 0.012/cm
UVA Reduction: 47.8%
3.0 mg/L 9800
Filtrate: 0.31 NTU
UVT: 96.6%
UVA: 0.014/cm
UVA Reduction: 39.1%
3.5 mg/L 9800
Filtrate: 0.15 NTU
UVT: 97.4%
UVA: 0.011/cm
UVA Reduction: 52.2%
4.0 mg/L 9800
Filtrate: 0.05 NTU
UVT: 98.0%
UVA: 0.008/cm
UVA Reduction: 65.2%

## Slide 16: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 9800

## Slide 17: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
4.0 mg/L 9800
Filtrate: 0.06 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 69.6%
4.5 mg/L 9800
Filtrate: 0.07 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 69.6%
5.0 mg/L 9800
Filtrate: 0.07 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 69.6%
5.5 mg/L 9800
Filtrate: 0.17 NTU
UVT: 98.0%
UVA: 0.007/cm
UVA Reduction: 65.2%

## Slide 18: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 960

## Slide 19: Jars 9-12: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
12 mg/L 960
Filtrate: 0.04 NTU
UVT: 98.1%
UVA: 0.008/cm
UVA Reduction: 65.2%
16 mg/L 960
Filtrate: 0.10 NTU
UVT: 98.0%
UVA: 0.008/cm
UVA Reduction: 65.2%
20 mg/L 960
Filtrate: 0.04 NTU
UVT: 98.6%
UVA: 0.006/cm
UVA Reduction: 73.9%
24 mg/L 960
Filtrate: 0.03 NTU
UVT: 98.6%
UVA: 0.006/cm
UVA Reduction: 73.9%

## Slide 20: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 960

## Slide 21: Jars 13-16: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NaOCl: 0
20 mg/L 960
Filtrate: 0.04 NTU
UVT: 98.6%
UVA: 0.006/cm
UVA Reduction: 73.9%
NaOCl: 3.0
20 mg/L 960
Filtrate: 0.12 NTU
UVT: 97.7%
UVA: 0.010/cm
UVA Reduction: 56.5%
NaOCl: 4.0
20 mg/L 960
Filtrate: 0.09 NTU
UVT: 97.7%
UVA: 0.010/cm
UVA Reduction: 56.5%
NaOCl: 5.0
20 mg/L 960
Filtrate: 0.03 NTU
UVT: 97.8%
UVA: 0.009/cm
UVA Reduction: 60.9%

## Slide 22: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 961

## Slide 23: Jars 17-20: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NaOCl: 0
16 mg/L 961
Filtrate: 0.03 NTU
UVT: 98.2%
UVA: 0.007/cm
UVA Reduction: 69.6%
NaOCl: 2.5
16 mg/L 961
Filtrate: 0.03 NTU
UVT: 97.9%
UVA: 0.009/cm
UVA Reduction: 60.9%
NaOCl: 0
20 mg/L 961
Filtrate: 0.05 NTU
UVT: 98.1%
UVA: 0.008/cm
UVA Reduction: 65.2%
NaOCl: 2.5
20 mg/L 961
Filtrate: 0.06 NTU
UVT: 97.6%
UVA: 0.010/cm
UVA Reduction: 56.52%

## Slide 24: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 9810

## Slide 25: Jars 21-24: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NaOCl: 0
3.6 mg/L 9810
Filtrate: 0.21 NTU
UVT: 98.2%
UVA: 0.011/cm
UVA Reduction: 52.2%
NaOCl: 2.5
3.6 mg/L 9810
Filtrate: 0.03 NTU
UVT: 98.0%
UVA: 0.008/cm
UVA Reduction: 65.2%
NaOCl: 0
4.0 mg/L 9810
Filtrate: 0.03 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 69.6%
NaOCl: 2.5
4.0 mg/L 9810
Filtrate: 0.04 NTU
UVT: 98.0%
UVA: 0.008/cm
UVA Reduction: 65.2%

## Slide 26: Jars 25-28 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulants 926/9890

## Slide 27: Jars 25-28: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
3.0 mg/L 926
Filtrate: 0.03 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 69.6%
3.6 mg/L 926
Filtrate: 0.12 NTU
UVT: 97.9%
UVA: 0.009/cm
UVA Reduction: 60.9%
3.0 mg/L 9890
Filtrate: 0.13 NTU
UVT: 97.5%
UVA: 0.010/cm
UVA Reduction: 56.5%
3.6 mg/L 9890
Filtrate: 0.36 NTU
UVT: 95.8%
UVA: 0.018/cm
UVA Reduction: 21.7%

## Slide 28: Jars 29-32 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 926

## Slide 29: Jars 29-32: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NaOCl: 0
2.6 mg/L 926
Filtrate: 0.14 NTU
UVT: 97.7%
UVA: 0.010/cm
UVA Reduction: 56.5%
NaOCl: 2.5
2.6 mg/L 926
Filtrate: 0.09 NTU
UVT: 97.5%
UVA: 0.010/cm
UVA Reduction: 56.5%
NaOCl: 0
3.0 mg/L 926
Filtrate: 0.05 NTU
UVT: 98.3%
UVA: 0.007/cm
UVA Reduction: 69.6%
NaOCl: 2.5
3.0 mg/L 926
Filtrate: 0.04 NTU
UVT: 98.1%
UVA: 0.008/cm
UVA Reduction: 65.2%

## Slide 30: Jars 33-35 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulants 926/9810/961

## Slide 31: Jars 33-35: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
NaOCl: 2.5
3.0 mg/L 926
Filtrate: 0.16 NTU
UVT: 97.0%
UVA: 0.013/cm
UVA Reduction: 43.5%
NaOCl: 2.5
4.0 mg/L 9810
Filtrate: 0.23 NTU
UVT: 96.3%
UVA: 0.016/cm
UVA Reduction: 30.4%
NaOCl: 2.5
20 mg/L 961
Filtrate: 0.03 NTU
UVT: 97.9%
UVA: 0.009/cm
UVA Reduction: 60.9%

## Slide 32: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 20-30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate). For this study, samples were taken immediately at the end of flocculation process.
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 33: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 34: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 35: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 36: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 37: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Jar Test Results/Procedures for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right video training https://youtu.be/aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732