## Slide 1: CSP-MacKerricher State Park CA2310301, Mendocino County Jar Test
by Guy Schott, P.E.
February 28, 2023

## Slide 2: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 3: CSP-MacKerricher State Park Source & Treated Water Characteristics, January 27, 2023
Source – Mill Creek
pH: 6.8 – 7.16
Alkalinity: x mg/L as CaCO3
Turbidity: 43 NTU
UVT: 23.3%,
UVA: 0.632/cm
0.4 um Filtered
Turbidity: 1.12 NTU
UVT: 60.2%,
UVA: 0.220/cm
Source – Iron Concentration
Fe: 11.7 mg/L

## Slide 4: Applied Coagulants for Jar Testing ()
960 (NTU Technologies)
33% Polyaluminum Hydroxychlorosulfate
67% Water
SG = 1.29
NSF limit: 250 mg/L as Product
BWS, Inc.
Greg Nieckarz, Ph.D.
Greg.niekarz@bws.works
541-953-5112
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 250 mg/L as Product

## Slide 5: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 6.8-7.16
LCA #1: CTC-00011: 51 mg/L
LCA #: 960: 78 mg/L

## Slide 6: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Ferric Chloride doses are reported as FeCl3.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 7: CSP-MacKerricher State Park; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | 960 mg/L | CTC-00011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min | %UVA Reduction | Filtrate Fe, mg/L
J1 | 40 | - | 0.07 | 79.7 | 0.098 | 32.1 | 55.5 | -
J2 | 50 | - | 0.24 | 89.0 | 0.050 | 20.6 | 77.3 | -
J3 | - | 40 | 0.70 | 81.6 | 0.087 | 12.2 | 60.5 | -
J4 | - | 50 | 0.71 | 82.9 | 0.081 | 9.97 | 63.2 | -
J5 | 60 | - | 0.28 | 83.7 | 0.076 | 59.4 | 65.5 | -
J6 | 70 | - | 0.08 | 85.1 | 0.069 | 65.4 | 68.6 | -
J7 |  | 60 | 0.92 | 82.7 | 0.082 | 8.54 | 62.7 | -
J8 |  | 70 | 0.08 | 86.3 | 0.063 | 10.1 | 71.4 | 6.8
J9 | 80 | - | 0.09 | 87.6 | 0.057 | 8.66 | 74.1 | -

## Slide 8: Jars 1-4 Test Flash Mix 200 RPM, 20 Sec Floc Mix 30 RPM, 5 min 25 mL sampled 5 minutes at end of Floc period Applied Coagulants 960 & CTC-00011

## Slide 9: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
40 mg/L CTC-00011
Filtrate: 0.07 NTU
UVT: 79.7%
UVA: 0.098/cm
UVA Reduction: 55.5%
Settled: 32.1 NTU
50 mg/L CTC-00011
Filtrate: 0.24 NTU
UVT: 89.0%
UVA: 0.050/cm
UVA Reduction: 77.3%
Settled: 20.6 NTU
40 mg/L 960
Filtrate: 0.70 NTU
UVT: 81.6%
UVA: 0.087/cm
UVA Reduction: 60.5%
Settled: 12.2 NTU
50 mg/L 960
Filtrate: 0.71 NTU
UVT: 82.9%
UVA: 0.081/cm
UVA Reduction: 63.2%
Settled: 9.97 NTU

## Slide 10: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 11: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
40 mg/L CTC-00011
Filtrate: 0.07 NTU
UVT: 79.7%
UVA: 0.098/cm
UVA Reduction: 55.5%
Settled: 32.1 NTU
50 mg/L CTC-00011
Filtrate: 0.24 NTU
UVT: 89.0%
UVA: 0.050/cm
UVA Reduction: 77.3%
Settled: 20.6 NTU
40 mg/L 960
Filtrate: 0.70 NTU
UVT: 81.6%
UVA: 0.087/cm
UVA Reduction: 60.5%
Settled: 12.2 NTU
50 mg/L 960
Filtrate: 0.71 NTU
UVT: 82.9%
UVA: 0.081/cm
UVA Reduction: 63.2%
Settled: 9.97 NTU

## Slide 12: Jars 5-8 Test Flash Mix 200 RPM, 20 Sec Floc Mix 30 RPM, 5 min 25 mL sampled 5 minutes at end of Floc period Applied Coagulants 960 & CTC-00011

## Slide 13: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
60 mg/L CTC-00011
Filtrate: 0.28 NTU
UVT: 83.7%
UVA: 0.076/cm
UVA Reduction: 65.5%
Settled: 59.4 NTU
70 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 85.1%
UVA: 0.069/cm
UVA Reduction: 68.6%
Settled: 65.4 NTU
60 mg/L 960
Filtrate: 0.92 NTU
UVT: 82.7%
UVA: 0.082/cm
UVA Reduction: 62.7%
Settled: 8.54 NTU
70 mg/L 960
Filtrate: 0.08 NTU
UVT: 86.3%
UVA: 0.063/cm
UVA Reduction: 71.4%
Settled: 10.1 NTU

## Slide 14: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 15: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L CTC-00011
Filtrate: 0.28 NTU
UVT: 83.7%
UVA: 0.076/cm
UVA Reduction: 65.5%
Settled: 59.4 NTU
70 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 85.1%
UVA: 0.069/cm
UVA Reduction: 68.6%
Settled: 65.4 NTU
60 mg/L 960
Filtrate: 0.92 NTU
UVT: 82.7%
UVA: 0.082/cm
UVA Reduction: 62.7%
Settled: 8.54 NTU
70 mg/L 960
Filtrate: 0.08 NTU
UVT: 86.3%
UVA: 0.063/cm
UVA Reduction: 71.4%
Settled: 10.1 NTU
Fe: 6.8 mg/L

## Slide 16: Jar 9 Test Flash Mix 200 RPM, 20 Sec Floc Mix 30 RPM, 5 min 25 mL sampled 5 minutes at end of Floc period Applied Coagulant 960

## Slide 17: Jar 9: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
80 mg/L 960
Filtrate: 0.09 NTU
UVT: 87.6%
UVA: 0.057/cm
UVA Reduction: 74.1%
Settled: 8.66 NTU

## Slide 18: Jar 9: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 19: Jar 9: After 25-minutes of settling, settled water turbidity is taken.
80 mg/L 960
Filtrate: 0.09 NTU
UVT: 87.6%
UVA: 0.057/cm
UVA Reduction: 74.1%
Settled: 8.66 NTU

## Slide 20: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 21: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 22: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 23: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 24: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 25: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732