## Slide 1: City of St. Helena CA2810004 Napa County Jar Test
by Guy Schott, P.E.
March 19, 2026

## Slide 2: Source Water: Bell Canyon Reservoir
Source Water Characteristics
Turbidity: 4.6 NTU
pH: 7.13
Alkalinity: 23.5 mg/L CaCO3
UVT: 65.34%,
UVA: 0.1848/cm
0.4 um Filtered
Turbidity: 1.13 NTU
UVT: 67.65%,
UVA: 0.1697/cm

## Slide 3: Flocculation/Sedimentation Basins

## Slide 4: UVT/UVA, pathlength 40 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Applied Coagulants for Jar Testing
Thatcher Company of CA
Ferric Sulfate
47.47% Ferric Sulfate (%, as Hydrate)
12.9% Ferric Iron
0% Basicity
SG = 1.576
NSF max use: 600 mg/L (product)
NTU Technologies
Zeta Floc 20, Organic Polymer
20% pDADMAC
80% Water
SG = 1.07
NSF limit: 50 mg/L as Product
NALCLEAR 8170 PULV (Nalco)
Flocculant
Dry Polyacrylamide
NSF max use: 1 mg/L

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.78
LCA #1
FeSO4-8.8 H2O: 60 mg/L
No pH adjustment.
Final pH: 5.08
LCA #2
FeSO4*8.8 H2O: 70 mg/L
NaOH added to keep pH at 5.5.

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Ferric sulfate is reported as hydrated Ferric Sulfate (FeSO4*8.8 H2O).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: City of St. Helena : Jar Test 1-8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar # | NaOH mg/L | FeSO4 *8.8 H2O mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | Final pH
J1 | 18 | 69 | 0.28 | 87.33 | 0.0589 | 65.3 | 8.8 | 6.49
J2 | 19 | 73 | 0.07 | 90.43 | 0.0437 | 74.2 | 7.32 | 6.49
J3 | 21 | 77 | 0.07 | 90.41 | 0.0438 | 74.2 | 6.45 | 6.48
J4 | 22 | 80 | 0.06 | 90.82 | 0.0418 | 75.4 | 1.92 | 6.47
J5 | 21 | 80 | 0.06 | 91.37 | 0.0392 | 76.9 | 5.8 | 6.31
J6 | 22 | 84 | 0.17 | 90.93 | 0.0413 | 75.7 | 6.36 | 6.32
J7 | 23 | 87 | 0.06 | 91.54 | 0.0384 | 77.4 | 5.86 | 6.35
J8 | 24 | 90 | 0.05 | 91.14 | 0.0403 | 76.3 | 1.89 | 6.58
Source water jar testing was taken after Post NaMnO4

## Slide 9: City of St. Helena : Jar Test 9-16 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar # | NaOH mg/L | FeSO4 *8.8 H2O mg/L | Nalco 8170 mg/L | Zeta Floc 20 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | Final pH
J9 | 20 | 80 | 0.3 | - | 0.20 | 89.93 | 0.0461 | 72.8 | 5.81 | -
J10 | 20 | 80 | - | 0.3 | 0.07 | 92.02 | 0.0362 | 78.7 | 3.76 | -
J11 | 20 | 80 | - | 0.5 | 0.14 | 91.36 | 0.0393 | 76.8 | 3.24 | -
J12 | 20 | 80 | - | 0.7 | 0.04 | 92.18 | 0.0354 | 79.1 | 3.01 | 6.40
J13 | 0 | 80 | - | - | 0.04 | 91.94 | 0.0365 | 78.5 | 3.12 | 3.95
J14 | 20 | 80 | - | - | 0.07 | 91.13 | 0.0403 | 76.3 | 5.89 | 6.34
J15 | 20 | 80 | 0.1 | - | 0.06 | 90.96 | 0.0412 | 75.7 | 4.77 | -
J16 | 20 | 80 | - | 1.0 | 0.04 | 91.99 | 0.0363 | 78.6 | 1.46 | -
Source water jar testing was taken after Post NaMnO4

## Slide 10: City of St. Helena : Jar Test 17-19 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar # | NaOH mg/L | FeSO4 *8.8 H2O mg/L | Zeta Floc 20 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | Final pH
J17 | 20 | 80 | 1.3 | 0.04 | 91.63 | 0.0380 | 77.6 | 2.67 | -
J18 | 20 | 80 | 1.6 | 0.04 | 92.12 | 0.0357 | 79.0 | 2.70 | 6.30
J19 | 20 | 80 | 1.9 | 0.04 | 92.18 | 0.0349 | 79.4 | 1.77 | -
Source water jar testing was taken after Post NaMnO4

## Slide 11: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Chemicals NaOH/FeSO4*8.8H2O

## Slide 12: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
NaOH: 18 mg/L
FeSO4*8.8 H2O: 69 mg/L
Filtrate: 0.28 NTU
UVT: 87.33%
UVA: 0.0589/cm
UVA Reduction: 65.3%
Settled: 8.8 NTU
pH: 6.49
NaOH: 19 mg/L
FeSO4*8.8 H2O: 73 mg/L
Filtrate: 0.07 NTU
UVT: 90.43%
UVA: 0.0437/cm
UVA Reduction: 74.2%
Settled: 7.3 NTU
pH: 6.49
NaOH: 21 mg/L
FeSO4*8.8 H2O: 77 mg/L
Filtrate: 0.07 NTU
UVT: 90.41%
UVA: 0.0438/cm
UVA Reduction: 74.2%
Settled: 7.3 NTU
pH: 6.48
NaOH: 22 mg/L
FeSO4*8.8 H2O: 80 mg/L
Filtrate: 0.06 NTU
UVT: 90.82%
UVA: 0.0418/cm
UVA Reduction: 75.4%
Settled: 1.92 NTU
pH: 6.47

## Slide 13: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 14: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
NaOH: 18 mg/L
FeSO4*8.8 H2O: 69 mg/L
Filtrate: 0.28 NTU
UVT: 87.33%
UVA: 0.0589/cm
UVA Reduction: 65.3%
Settled: 8.8 NTU
pH: 6.49
NaOH: 19 mg/L
FeSO4*8.8 H2O: 73 mg/L
Filtrate: 0.07 NTU
UVT: 90.43%
UVA: 0.0437/cm
UVA Reduction: 74.2%
Settled: 7.3 NTU
pH: 6.49
NaOH: 21 mg/L
FeSO4*8.8 H2O: 77 mg/L
Filtrate: 0.07 NTU
UVT: 90.41%
UVA: 0.0438/cm
UVA Reduction: 74.2%
Settled: 7.3 NTU
pH: 6.48
NaOH: 22 mg/L
FeSO4*8.8 H2O: 80 mg/L
Filtrate: 0.06 NTU
UVT: 90.82%
UVA: 0.0418/cm
UVA Reduction: 75.4%
Settled: 1.92 NTU
pH: 6.47

## Slide 15: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Chemicals NaOH/FeSO4*8.8H2O

## Slide 16: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
NaOH: 21 mg/L
FeSO4*8.8 H2O: 80 mg/L
Filtrate: 0.06 NTU
UVT: 91.37%
UVA: 0.0392/cm
UVA Reduction: 76.9%
Settled: 5.8 NTU
pH: 6.31
NaOH: 22 mg/L
FeSO4*8.8 H2O: 84 mg/L
Filtrate: 0.17 NTU
UVT: 90.93%
UVA: 0.0413/cm
UVA Reduction: 75.7%
Settled: 6.36 NTU
pH: 6.32
NaOH: 23 mg/L
FeSO4*8.8 H2O: 87 mg/L
Filtrate: 0.06 NTU
UVT: 90.93%
UVA: 0.0384/cm
UVA Reduction: 77.4%
Settled: 5.86 NTU
pH: 6.35
NaOH: 24 mg/L
FeSO4*8.8 H2O: 90 mg/L
Filtrate: 0.05 NTU
UVT: 91.14%
UVA: 0.0403/cm
UVA Reduction: 76.3%
Settled: 1.89 NTU
pH: 6.58

## Slide 17: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Chemicals NaOH/FeSO4*8.8H2O Nalco 8170/ZetaFloc 20

## Slide 18: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
Nalco 8170: 0.3 mg/L
Filtrate: 0.20 NTU
UVT: 91.37%
UVA: 0.0461/cm
UVA Reduction: 72.8%
Settled: 5.81 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 0.3 mg/L
Filtrate: 0.07 NTU
UVT: 92.02%
UVA: 0.0362/cm
UVA Reduction: 78.7%
Settled: 3.76 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 0.5 mg/L
Filtrate: 0.14 NTU
UVT: 91.36%
UVA: 0.0393/cm
UVA Reduction: 76.8%
Settled: 3.24 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 0.7 mg/L
Filtrate: 0.04 NTU
UVT: 92.18%
UVA: 0.0354/cm
UVA Reduction: 79.1%
Settled: 3.01 NTU
pH: 6.40

## Slide 19: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 20: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
Nalco 8170: 0.3 mg/L
Filtrate: 0.20 NTU
UVT: 91.37%
UVA: 0.0461/cm
UVA Reduction: 72.8%
Settled: 5.81 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 0.3 mg/L
Filtrate: 0.07 NTU
UVT: 92.02%
UVA: 0.0362/cm
UVA Reduction: 78.7%
Settled: 3.76 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 0.5 mg/L
Filtrate: 0.14 NTU
UVT: 91.36%
UVA: 0.0393/cm
UVA Reduction: 76.8%
Settled: 3.24 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 0.7 mg/L
Filtrate: 0.04 NTU
UVT: 92.18%
UVA: 0.0354/cm
UVA Reduction: 79.1%
Settled: 3.01 NTU
pH: 6.40

## Slide 21: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Chemicals NaOH/FeSO4*8.8H2O Nalco 8170/ZetaFloc 20

## Slide 22: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
NaOH: 0 mg/L
FeSO4*8.8 H2O: 80 mg/L
Filtrate: 0.04 NTU
UVT: 91.69%
UVA: 0.0365/cm
UVA Reduction: 78.5%
Settled: 3.12 NTU
pH: 3.95
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
Nalco 8170: 0.1 mg/L
Filtrate: 0.06 NTU
UVT: 90.96%
UVA: 0.0412/cm
UVA Reduction: 75.7%
Settled: 4.77 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
Filtrate: 0.07 NTU
UVT: 91.13%
UVA: 0.0403/cm
UVA Reduction: 76.3%
Settled: 5.89 NTU
pH: 6.34
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 1.0 mg/L
Filtrate: 0.04 NTU
UVT: 91.99%
UVA: 0.0363/cm
UVA Reduction: 78.6%
Settled: 1.46 NTU

## Slide 23: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 24: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
NaOH: 0 mg/L
FeSO4*8.8 H2O: 80 mg/L
Filtrate: 0.04 NTU
UVT: 91.69%
UVA: 0.0365/cm
UVA Reduction: 78.5%
Settled: 3.12 NTU
pH: 3.95
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
Nalco 8170: 0.1 mg/L
Filtrate: 0.06 NTU
UVT: 90.96%
UVA: 0.0412/cm
UVA Reduction: 75.7%
Settled: 4.77 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
Filtrate: 0.07 NTU
UVT: 91.13%
UVA: 0.0403/cm
UVA Reduction: 76.3%
Settled: 5.89 NTU
pH: 6.34
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 1.0 mg/L
Filtrate: 0.04 NTU
UVT: 91.99%
UVA: 0.0363/cm
UVA Reduction: 78.6%
Settled: 1.46 NTU

## Slide 25: Jars 17-19 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Chemicals NaOH/FeSO4*8.8H2O ZetaFloc 20

## Slide 26: Jars 17-19: End of 5-minute flocculation (30 RPM) duration.
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 1.3 mg/L
Filtrate: 0.04 NTU
UVT: 91.63%
UVA: 0.0380/cm
UVA Reduction: 77.6%
Settled: 2.67 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 1.6 mg/L
Filtrate: 0.04 NTU
UVT: 92.12%
UVA: 0.0357/cm
UVA Reduction: 79.0%
Settled: 2.70 NTU
pH: 6.30
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 1.9 mg/L
Filtrate: 0.04 NTU
UVT: 92.18%
UVA: 0.0354/cm
UVA Reduction: 79.4%
Settled: 1.77 NTU

## Slide 27: Jars 17-19: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 28: Jars 17-19: After 25-minutes of settling, settled water turbidity is taken.
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 1.3 mg/L
Filtrate: 0.04 NTU
UVT: 91.63%
UVA: 0.0380/cm
UVA Reduction: 77.6%
Settled: 2.67 NTU
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 1.6 mg/L
Filtrate: 0.04 NTU
UVT: 92.12%
UVA: 0.0357/cm
UVA Reduction: 79.0%
Settled: 2.70 NTU
pH: 6.30
NaOH: 20 mg/L
FeSO4*8.8 H2O: 80 mg/L
ZetaFloc 20 : 1.9 mg/L
Filtrate: 0.04 NTU
UVT: 92.18%
UVA: 0.0354/cm
UVA Reduction: 79.4%
Settled: 1.77 NTU

## Slide 29: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 30: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 31: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 32: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 33: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 34: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732