## Slide 1: City of St. Helena CA2810004 Napa County Jar Test
by Guy Schott, P.E.
April 5, 2019

## Slide 2: Source Water: Bell Canyon Reservoir
Source Water Characteristics
Turbidity: 5.7 NTU
pH: 7.2
UVT: 63.2%
UVA: 0.199
0.4 um Filtered
UVT: 68.6%
UVA: 0.164

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Applied Coagulants for Jar Testing (1)
Aluminum Sulfate (Product)
Al2(SO4)3*14.3H20 (Liquid)
48% Aluminum Sulfate
52% Water
8.2% Al2O3
4.3% Al
0% Basicity
SG = 1.32
NSF limit: 400 mg/L (product)
As hydrated Al2(SO4)3*14.3H20
17% Al2O3
NALCLEAR 8170 PULV (Nalco)
Flocculant
Dry
Polyacrylamide
NSF limit: 1 mg/L

## Slide 5: Applied Coagulants for Jar Testing (2)
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product
10 mg/L as 9800 = Reduction 1.18 mg/L as CaCO3
Pro Pac 926 (NTU Technologies)
30-40% Aluminum Chlorohydrate
30% polyamine (80% water, 20% active polyamines)
30-40% Water
~14.17% Al2O3
~7.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 83 mg/L as Product;
Product dose 16.6 mg/L = 1 mg/L polyamines active

## Slide 6: Polyamine C59H108N14O10 MW: 1,173.6 g/mol

## Slide 7: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.2
LCA #1
9800: 24 mg/L as product
No pH adjustment.
LCA #2:
Aluminum Sulfate: 32 mg/L as Alum
No pH adjustment.

## Slide 8: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Aluminum sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 9: City of St. Helena : Jar Test 1-8 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (10 min)
Jar # | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 22 | 0.71 | 87.6 | 0.057 | 65.2 | 3.3
J2 | 24 | 0.20 | 91.0 | 0.041 | 75.0 | 2.9
J3 | 26 | 0.12 | 91.9 | 0.037 | 77.5 | 2.3
J4 | 28 | 0.10 | 92.4 | 0.034 | 79.3 | 1.9
J5 | 26 | 0.11 | 91.9 | 0.037 | 77.4 | 2.8
J6 | 28 | 0.07 | 92.8 | 0.032 | 80.4 | 2.3
J7 | 30 | 0.08 | 93.0 | 0.032 | 80.4 | 3.0
J8 | 32 | 0.08 | 93.2 | 0.031 | 81.1 | 2.8

## Slide 10: Veterans Home: Jar Test 9-14 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (10 min)
Jar # | NaOCl mg/L | PAC mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 0 | 20 | 26 | 0.07 | 92.8 | 0.032 | 80.5 | 7.0
J10 | 0 | 20 | 28 | 0.18 | 92.8 | 0.032 | 80.5 | 5.0
J11 | 0 | 20 | 30 | 0.07 | 93.4 | 0.030 | 81.7 | 4.4
J12 | 0 | 20 | 32 | 0.49 | 93.1 | 0.031 | 81.1 | 5.4
J13 | 1.5 | 0 | 28 | 0.73 | 89.0 | 0.051 | 68.9 | 1.8
J14 | 1.5 | 0 | 30 | 0.62 | 90.4 | 0.044 | 73.2 | 1.7

## Slide 11: Veterans Home: Jar Test 15-20 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (10 min)
Jar # | 926 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J15 | 28 | 0.47 | 90.1 | 0.045 | 72.6 | 1.8
J16 | 30 | 0.39 | 91.2 | 0.040 | 75.6 | 1.6
J17 | 32 | 0.07 | 93.3 | 0.030 | 81.7 | 3.4
J18 | 34 | 0.05 | 93.9 | 0.027 | 83.5 | 3.1
J19 | 36 | 0.23 | 92.8 | 0.032 | 80.5 | 6.1
J20 | 38 | 0.12 | 93.8 | 0.028 | 82.9 | 6.3

## Slide 12: Veterans Home: Jar Test 21-24 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (10 min)
Jar # | Alum mg/L | 8107 mg/L | PAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J21 | 28 | 0.2 | 0 | 0.06 | 92.1 | 0.036 | 78.0 | 1.6
J22 | 30 | 0.2 | 0 | 0.06 | 92.9 | 0.032 | 80.5 | 1.6
J23 | 28 | 0.2 | 20 | 0.09 | 92.2 | 0.035 | 78.7 | 2.2
J24 | 30 | 0.2 | 20 | 0.11 | 92.6 | 0.033 | 79.9 | 1.7

## Slide 13: Veterans Home: Jar Test 25-28 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (10 min)
Jar # | Alum mg/L | 8107 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 28 | 0.2 | 0.19 | 92.2 | 0.035 | 78.7 | 1.8
J26 | 30 | 0.2 | 0.17 | 92.5 | 0.034 | 79.3 | 1.6
J27 | 32 | 0.2 | 0.07 | 92.4 | 0.034 | 79.3 | 1.8
J28 | 34 | 0.2 | 0.07 | 93.2 | 0.031 | 81.1 | 3.8

## Slide 14: Veterans Home: Jar Test 29-36 Results Flash Mix 200 RPM (60 sec); Floc Mix 30 RPM (10 min)
Jar # | 926 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J29 | 32 | 0.43 | 90.8 | 0.042 | 74.4 | 1.8
J30 | 34 | 0.06 | 93.7 | 0.028 | 82.9 | 2.2
J31 | 36 | 0.63 | 90.5 | 0.043 | 73.8 | 3.5
J32 | 38 | 0.50 | 91.3 | 0.040 | 75.6 | 6.4
J33 | 33 | 0.11 | 93.2 | 0.031 | 81.1 | 1.9
J34 | 33 | 0.07 | 93.4 | 0.030 | 81.7 | 1.8
J35 | 34 | 0.07 | 93.2 | 0.031 | 81.1 | 2.5
J36 | 34 | 0.06 | 94.0 | 0.027 | 83.5 | 2.9

## Slide 15: Jars 1-4 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Post NaMnO4 Applied Coagulant 9800

## Slide 16: Jars 1-4: End of 10-minute flocculation (30 RPM) duration.
22mg/L 9800
Filtrate: 0.71 NTU
UVT: 87.6%
UVA: 0.057/cm
UVA Reduction: 65.2%
Settled: 3.3 NTU
24 mg/L 9800
Filtrate: 0.20 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction: 75.0%
Settled: 2.9 NTU
26 mg/L 9800
Filtrate: 0.12 NTU
UVT: 91.9%
UVA: 0.037/cm
UVA Reduction: 77.5%
Settled: 2.3 NTU
28 mg/L 9800
Filtrate: 0.10 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 77.5%
Settled: 1.9 NTU

## Slide 17: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 18: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
22mg/L 9800
Filtrate: 0.71 NTU
UVT: 87.6%
UVA: 0.057/cm
UVA Reduction: 65.2%
Settled: 3.3 NTU
24 mg/L 9800
Filtrate: 0.20 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction: 75.0%
Settled: 2.9 NTU
26 mg/L 9800
Filtrate: 0.12 NTU
UVT: 91.9%
UVA: 0.037/cm
UVA Reduction: 77.5%
Settled: 2.3 NTU
28 mg/L 9800
Filtrate: 0.10 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 77.5%
Settled: 1.9 NTU

## Slide 19: Jars 5-8 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Post NaMnO4 Applied Coagulant 9800

## Slide 20: Jars 5-8: End of 10-minute flocculation (30 RPM) duration.
26 mg/L 9800
Filtrate: 0.11 NTU
UVT: 91.9%
UVA: 0.037/cm
UVA Reduction: 77.4%
Settled: 2.8 NTU
28 mg/L 9800
Filtrate: 0.07 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 80.4%
Settled: 2.3 NTU
30 mg/L 9800
Filtrate: 0.08 NTU
UVT: 93.0%
UVA: 0.032/cm
UVA Reduction: 80.4%
Settled: 3.0 NTU
32 mg/L 9800
Filtrate: 0.08 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 2.8 NTU

## Slide 21: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 22: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
26 mg/L 9800
Filtrate: 0.11 NTU
UVT: 91.9%
UVA: 0.037/cm
UVA Reduction: 77.4%
Settled: 2.8 NTU
28 mg/L 9800
Filtrate: 0.07 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 80.4%
Settled: 2.3 NTU
30 mg/L 9800
Filtrate: 0.08 NTU
UVT: 93.0%
UVA: 0.032/cm
UVA Reduction: 80.4%
Settled: 3.0 NTU
32 mg/L 9800
Filtrate: 0.08 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 2.8 NTU

## Slide 23: Jars 9-12 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Post NaMnO4 Applied Coagulant 9800 w/PAC

## Slide 24: Jars 9-12: End of 10-minute flocculation (30 RPM) duration.
20 mg/L PAC
26 mg/L 9800
Filtrate: 0.07 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 80.5%
Settled: 7.0 NTU
20 mg/L PAC
28 mg/L 9800
Filtrate: 0.18 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 80.5%
Settled: 5.0 NTU
20 mg/L PAC
30 mg/L 9800
Filtrate: 0.07 NTU
UVT: 93.4%
UVA: 0.030/cm
UVA Reduction: 81.7%
Settled: 4.4 NTU
20 mg/L PAC
32 mg/L 9800
Filtrate: 0.49 NTU
UVT: 93.1%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 5.4 NTU

## Slide 25: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 26: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L PAC
26 mg/L 9800
Filtrate: 0.07 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 80.5%
Settled: 7.0 NTU
20 mg/L PAC
28 mg/L 9800
Filtrate: 0.18 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 80.5%
Settled: 5.0 NTU
20 mg/L PAC
30 mg/L 9800
Filtrate: 0.07 NTU
UVT: 93.4%
UVA: 0.030/cm
UVA Reduction: 81.7%
Settled: 4.4 NTU
20 mg/L PAC
32 mg/L 9800
Filtrate: 0.49 NTU
UVT: 93.1%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 5.4 NTU

## Slide 27: Jars 13-16 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Post NaMnO4 Applied Coagulants 9800/926 w/NaOCl

## Slide 28: Jars 13-16: End of 10-minute flocculation (30 RPM) duration.
1.5 mg/L NaOCl
28 mg/L 9800
Filtrate: 0.73 NTU
UVT: 89.0%
UVA: 0.051/cm
UVA Reduction: 68.9%
Settled: 1.8 NTU
1.5 mg/L NaOCl
30 mg/L 9800
Filtrate: 0.62 NTU
UVT: 90.4%
UVA: 0.044/cm
UVA Reduction: 73.2%
Settled: 1.7 NTU
0 mg/L NaOCl
28 mg/L 926
Filtrate: 0.47 NTU
UVT: 90.4%
UVA: 0.045/cm
UVA Reduction: 72.6%
Settled: 1.8 NTU
0 mg/L NaOCl
30 mg/L 926
Filtrate: 0.39 NTU
UVT: 91.2%
UVA: 0.040/cm
UVA Reduction: 75.6%
Settled: 1.6 NTU

## Slide 29: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 30: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
1.5 mg/L NaOCl
28 mg/L 9800
Filtrate: 0.73 NTU
UVT: 89.0%
UVA: 0.051/cm
UVA Reduction: 68.9%
Settled: 1.8 NTU
1.5 mg/L NaOCl
30 mg/L 9800
Filtrate: 0.62 NTU
UVT: 90.4%
UVA: 0.044/cm
UVA Reduction: 73.2%
Settled: 1.7 NTU
0 mg/L NaOCl
28 mg/L 926
Filtrate: 0.47 NTU
UVT: 90.4%
UVA: 0.045/cm
UVA Reduction: 72.6%
Settled: 1.8 NTU
0 mg/L NaOCl
30 mg/L 926
Filtrate: 0.39 NTU
UVT: 91.2%
UVA: 0.040/cm
UVA Reduction: 75.6%
Settled: 1.6 NTU

## Slide 31: Jars 17-20 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Post NaMnO4 Applied Coagulant 926

## Slide 32: Jars 17-20: End of 10-minute flocculation (30 RPM) duration.
32 mg/L 926
Filtrate: 0.07 NTU
UVT: 93.3%
UVA: 0.030/cm
UVA Reduction: 81.7%
Settled: 3.4 NTU
34 mg/L 926
Filtrate: 0.05 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 83.5%
Settled: 3.1 NTU
36 mg/L 926
Filtrate: 0.23 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 80.5%
Settled: 6.1 NTU
38 mg/L 926
Filtrate: 0.12 NTU
UVT: 93.8%
UVA: 0.028/cm
UVA Reduction: 82.9%
Settled: 6.3 NTU

## Slide 33: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 34: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
32 mg/L 926
Filtrate: 0.07 NTU
UVT: 93.3%
UVA: 0.030/cm
UVA Reduction: 81.7%
Settled: 3.4 NTU
34 mg/L 926
Filtrate: 0.05 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 83.5%
Settled: 3.1 NTU
36 mg/L 926
Filtrate: 0.23 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 80.5%
Settled: 6.1 NTU
38 mg/L 926
Filtrate: 0.12 NTU
UVT: 93.8%
UVA: 0.028/cm
UVA Reduction: 82.9%
Settled: 6.3 NTU

## Slide 35: Jars 21-24 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/8170

## Slide 36: Jars 21-24: End of 10-minute flocculation (30 RPM) duration.
28 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.06 NTU
0 mg/L PAC
UVT: 92.1%
UVA: 0.036/cm
UVA Reduction: 78.0%
Settled: 1.6 NTU
30 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.06 NTU
0 mg/L PAC
UVT: 92.9%
UVA: 0.032/cm
UVA Reduction: 80.5%
Settled: 1.6 NTU
28 mg/L Alum
0.2 mg/L 8170
20 mg/L PAC
Filtrate: 0.09 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 78.7%
Settled: 2.2 NTU
28 mg/L Alum
0.2 mg/L 8170
20 mg/L PAC
Filtrate: 0.11 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 79.9%
Settled: 1.7 NTU

## Slide 37: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 38: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
28 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.06 NTU
0 mg/L PAC
UVT: 92.1%
UVA: 0.036/cm
UVA Reduction: 78.0%
Settled: 1.6 NTU
30 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.06 NTU
0 mg/L PAC
UVT: 92.9%
UVA: 0.032/cm
UVA Reduction: 80.5%
Settled: 1.6 NTU
28 mg/L Alum
0.2 mg/L 8170
20 mg/L PAC
Filtrate: 0.09 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 78.7%
Settled: 2.2 NTU
28 mg/L Alum
0.2 mg/L 8170
20 mg/L PAC
Filtrate: 0.11 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 79.9%
Settled: 1.7 NTU

## Slide 39: Jars 25-28 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Pre-NaMnO4 Applied Coagulants Alum/8170

## Slide 40: Jars 25-28: End of 10-minute flocculation (30 RPM) duration.
28 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.19 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 78.7%
Settled: 1.8 NTU
30 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.17 NTU
UVT: 92.5%
UVA: 0.034/cm
UVA Reduction: 79.3%
Settled: 1.6 NTU
32 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.07 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 79.3%
Settled: 1.8 NTU
34 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.07 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 3.8 NTU

## Slide 41: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 42: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
28 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.19 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 78.7%
Settled: 1.8 NTU
30 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.17 NTU
UVT: 92.5%
UVA: 0.034/cm
UVA Reduction: 79.3%
Settled: 1.6 NTU
32 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.07 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 79.3%
Settled: 1.8 NTU
34 mg/L Alum
0.2 mg/L 8170
Filtrate: 0.07 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 3.8 NTU

## Slide 43: Jars 29-32 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Pre-NaMnO4 Applied Coagulant 926

## Slide 44: Jars 29-32: End of 10-minute flocculation (30 RPM) duration.
32 mg/L 926
Filtrate: 0.43 NTU
UVT: 90.8%
UVA: 0.042/cm
UVA Reduction: 74.4%
Settled: 1.8 NTU
34 mg/L 926
Filtrate: 0.06 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 82.9%
Settled: 2.2 NTU
36 mg/L 926
Filtrate: 0.63 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction: 73.8%
Settled: 3.5 NTU
38 mg/L 926
Filtrate: 0.50 NTU
UVT: 91.3%
UVA: 0.040/cm
UVA Reduction: 75.6%
Settled: 6.4 NTU

## Slide 45: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 46: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
32 mg/L 926
Filtrate: 0.43 NTU
UVT: 90.8%
UVA: 0.042/cm
UVA Reduction: 74.4%
Settled: 1.8 NTU
34 mg/L 926
Filtrate: 0.06 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 82.9%
Settled: 2.2 NTU
36 mg/L 926
Filtrate: 0.63 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction: 73.8%
Settled: 3.5 NTU
38 mg/L 926
Filtrate: 0.50 NTU
UVT: 91.3%
UVA: 0.040/cm
UVA Reduction: 75.6%
Settled: 6.4 NTU

## Slide 47: Jars 33-36 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Pre-NaMnO4 Applied Coagulant 926

## Slide 48: Jars 33-36: End of 10-minute flocculation (30 RPM) duration.
33 mg/L 926
Filtrate: 0.11 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 1.9 NTU
33 mg/L 926
Filtrate: 0.07 NTU
UVT: 93.4%
UVA: 0.030/cm
UVA Reduction: 81.7%
Settled: 1.8 NTU
34 mg/L 926
Filtrate: 0.07 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 2.5 NTU
34 mg/L 926
Filtrate: 0.06 NTU
UVT: 94.0%
UVA: 0.027/cm
UVA Reduction: 83.5%
Settled: 2.9 NTU

## Slide 49: Jars 33-36: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 50: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
33 mg/L 926
Filtrate: 0.11 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 1.9 NTU
33 mg/L 926
Filtrate: 0.07 NTU
UVT: 93.4%
UVA: 0.030/cm
UVA Reduction: 81.7%
Settled: 1.8 NTU
34 mg/L 926
Filtrate: 0.07 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 81.1%
Settled: 2.5 NTU
34 mg/L 926
Filtrate: 0.06 NTU
UVT: 94.0%
UVA: 0.027/cm
UVA Reduction: 83.5%
Settled: 2.9 NTU

## Slide 51: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 52: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 53: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 54: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 55: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 56: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732