## Slide 1: Heritage Ranch CSD CA4010012 San Luis Obispo County Jar Test
by Guy Schott, P.E.
September 27, 2022

## Slide 2: Lake Nacimiento

## Slide 3: Source Water/Intake
Source Water: Well 01 (Nacimiento River)
Pump Station Well 01 (Nacimiento River)

## Slide 4: Lamella Inclined Plate Clarifier

## Slide 5: Flash/Floc Mixer
Coagulant Injection Point

## Slide 6: Flash/Floc Mixer and Plate Settler
Flash Mixer
Floc Mixer
Plate
Settler

## Slide 7: Plate Settler
Plate Settler
Overflow weir

## Slide 8: Roberts Filtration Plant 4 x Trains (350 gpm per skid)

## Slide 9: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 10: Heritage Ranch CSD, September 27, 2022 Treatment Plant: Plate Settlers followed by Roberts Filtration Source Water Characteristics,
Source
pH: 7.64
Alkalinity: 108 mg/L as CaCO3
Turbidity: 4.3 NTU
UVT: 65.7%,
UVA: 0.181/cm
0.4 um Filtered
Turbidity: 0.38 NTU
UVT: 68.8%,
UVA: 0.162/cm
Post Plate Settler
3.4 - 3.6 NTU
(applied to Roberts Filtration Plant)
Plant Filtrate Water
pH: 7.41
Alkalinity: 99 mg/L as CaCO3
Turbidity: 0.12 NTU
UVT: 83.1%,
UVA: 0.080/cm

## Slide 11: Applied Coagulants for Jar Testing (1)
Aluminum Sulfate (Product)
Al2(SO4)3*14.3H20 (Liquid)
48% Aluminum Sulfate
52% Water
8.2% Al2O3
4.3% Al
0% Basicity
SG = 1.32
NSF limit: 400 mg/L (product)
As hydrated Al2(SO4)3*14.3H20
17% Al2O3
Brenntag (559-485-4150)
Praestol organic polymer 186K
SG = 1.1
Product Viscosity: 60-180 centipoise
Molecular Weight: 150,000 g/moles
pDADMAC (20% active, 80% H2O)
NSF limit: 50 mg/L (product)
Product dose 5 mg/L = 1 mg/L pDADMAC active

## Slide 12: Applied Coagulants for Jar Testing (2)
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 40 mg/L = 1 mg/L polyamines active
Pro Pac 9890 (NTU Technologies)
45-50% Aluminum Chlorohydrate
45-50% Water
~18.9% Al2O3
~10% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 40 mg/L = 1 mg/L polyamines active

## Slide 13: Applied Coagulants for Jar Testing (3)
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product;

## Slide 14: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.64
LCA #1: Alum: 47 mg/L as hydrated
pH adjusted to 6.6 with acetic acid
LCA #2: 9800: 63 mg/L
No pH adjustment

## Slide 15: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 16: Source Water (pH: 7.64, Alkalinity: 108 mg/L)
Coagulant | Chemical Dose, mg/L | Alkalinity Consumed mg/L as CaCO3 | Treated Water Alkalinity mg/L as CaCO3 | Treated Water pH
Alum | 10 | 5 | 103 | 7.40
Alum | 15 | 7.5 | 100.5 | 7.25
Alum | 40 | 20 | 88 | 6.97
Alum | 70 | 35.1 | 73 | 6.72
Alum | 100 | 50.1 | 58 | 6.54
Alum/9890 | 40/10 | 21 | 87 | 7.05
Alum/9890 | 60/10 | 31 | 77 | 6.87
Alum/9890 | 80/10 | 41 | 67 | 6.70
9810 | 70 | 7.9 | 100 | 7.42
9810 | 90 | 10.1 | 98 | 7.38

## Slide 17: Heritage Ranch CSD; Source Well 01 (Nacimiento River) Summary of Plant Coagulant/Dose Jar vs. Optimum Dose and Coagulants
Jar# | Na- MnO4 mg/L | Alum (dry) mg/L | 186K pDADMAC mg/L | 9890 mg/L | 9800 mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Re- duction | Settle NTU 25 min
65 | 1.2 | 15 | 6.0 | - | - | - | 0.09 | 82.5 | 0.083 | 48.8 | 3.6
vs. |  |  |  |  |  |  |  |  |  |  | 
17 | 0 | 100 | 0 | - | - | - | 0.06 | 91.1 | 0.040 | 75.3 | 1.3
66 | 1.2 | 100 | 6.0 | - | - | - | 0.07 | 91.3 | 0.039 | 75.9 | 1.5
55 | 1.2 | 60 | - | 10 | - | - | 0.06 | 89.9 | 0.045 | 72.2 | 1.3
11 | 0 | - | - | - | 80 | - | 0.05 | 90.3 | 0.044 | 72.8 | 1.2
50 | 0 | - | - | - | - | 70 | 0.05 | 90.9 | 0.041 | 74.7 | 0.80
49 | 1.2 | - | - | - | - | 70 | 0.05 | 90.1 | 0.037 | 77.2 | 0.49
16 | 0 | - | - | - | - | 90 | 0.05 | 91.4 | 0.038 | 76.5 | 0.57
52 | 1.2 | - | - |  |  | 90 | 0.06 | 92.3 | 0.034 | 79.0 | 0.45

## Slide 18: Heritage Ranch CSD; Source Well 01; Jar Test 1 - 8 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum (dry) mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 20 | 0.63 | 77.9 | 0.108 | 34.6 | 6.3
J2 | 30 | 0.81 | 77.1 | 0.112 | 30.9 | 6.1
J3 | 40 | 0.72 | 80.5 | 0.094 | 42.0 | 5.6
J4 | 50 | 0.12 | 86.1 | 0.064 | 60.5 | 2.5
J5 | 60 | 0.18 | 87.1 | 0.059 | 63.6 | 2.2
J6 | 70 | 0.12 | 87.7 | 0.056 | 65.4 | 2.0
J7 | 80 | 0.14 | 88.3 | 0.053 | 67.3 | 2.2
J8 | 90 | 0.14 | 89.3 | 0.049 | 69.8 | 2.2

## Slide 19: Heritage Ranch CSD; Source Well 01; Jar Test 9 - 16 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 9800 mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 60 | - | 0.06 | 89.1 | 0.050 | 69.1 | 1.7
J10 | 70 | - | 0.05 | 89.9 | 0.046 | 71.6 | 1.2
J11 | 80 | - | 0.05 | 90.3 | 0.044 | 72.8 | 1.2
J12 | 90 | - | 0.07 | 90.5 | 0.043 | 73.5 | 1.4
J13 | - | 60 | 0.05 | 90.0 | 0.045 | 72.2 | 0.72
J14 | - | 70 | 0.12 | 90.1 | 0.045 | 72.2 | 0.46
J15 | - | 80 | 0.05 | 91.1 | 0.040 | 75.3 | 0.44
J16 | - | 90 | 0.05 | 91.4 | 0.038 | 76.5 | 0.57

## Slide 20: Heritage Ranch CSD; Source Well 01; Jar Test 17 - 24 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum (dry) mg/L | 186K pDADMAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 100 | - | 0.06 | 91.1 | 0.040 | 75.3 | 1.3
J18 | 110 | - | 0.07 | 91.0 | 0.040 | 75.3 | 1.9
J19 | 120 | - | 0.07 | 91.0 | 0.040 | 75.3 | 2.6
J20 | 130 | - | 0.07 | 91.2 | 0.039 | 75.9 | 2.1
J21 | 70 | 3.0 | 0.10 | 89.1 | 0.049 | 69.8 | 1.4
J22 | 80 | 3.0 | 0.06 | 89.5 | 0.047 | 71.0 | 1.5
J23 | 90 | 3.0 | 0.10 | 90.4 | 0.043 | 73.5 | 1.5
J24 | 90 | 3.0 | 0.10 | 90.3 | 0.044 | 72.8 | 1.6

## Slide 21: Heritage Ranch CSD; Source Well 01; Jar Test 25 - 32 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | PAC mg/L | Alum (dry) mg/L | 186K pDADMAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 0 | 100 | - | 0.16 | 89.2 | 0.049 | 69.8 | 1.7
J26 | 5 | 100 | - | 0.43 | 88.5 | 0.052 | 67.9 | 1.6
J27 | 10 | 100 | - | 0.26 | 89.5 | 0.048 | 70.4 | 2.0
J28 | 15 | 100 | - | 0.22 | 89.7 | 0.047 | 71.0 | 1.1
J29 | 0 | 100 | 3.0 | 0.13 | 90.0 | 0.045 | 72.2 | 1.9
J30 | 5 | 100 | 3.0 | 0.09 | 90.6 | 0.042 | 74.1 | 1.7
J31 | 10 | 100 | 3.0 | 0.05 | 91.0 | 0.041 | 74.7 | 2.1
J32 | 15 | 100 | 3.0 | 0.04 | 91.3 | 0.039 | 75.9 | 1.7

## Slide 22: Heritage Ranch CSD; Source Well 01; Jar Test 33 - 36 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | PAC mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J33 | 0 | 80 | 0.13 | 89.9 | 0.046 | 71.6 | 1.1
J34 | 5 | 80 | 0.24 | 88.9 | 0.050 | 65.4 | 1.4
J35 | 10 | 80 | 0.07 | 90.4 | 0.043 | 73.5 | 1.4
J36 | 15 | 80 | 0.09 | 90.5 | 0.043 | 73.5 | 1.3

## Slide 23: Heritage Ranch CSD; Source Well 01; Jar Test 37 - 40 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 961 Mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J37 | 60 | 0.06 | 88.7 | 0.051 | 68.5 | 3.6
J38 | 70 | 0.09 | 89.0 | 0.050 | 69.1 | 6.6
J39 | 80 | 0.36 | 86.7 | 0.062 | 61.7 | 6.3
J40 | 90 | 1.23 | 80.0 | 0.097 | 40.1 | 6.2

## Slide 24: Heritage Ranch CSD; Source Well 01; Jar Test 41 - 48 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | NaMnO4 mg/L | Alum (dry) mg/L | 186K pDADMAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J41 | 0 | 100 | 4.0 | 0.06 | 89.8 | 0.046 | 71.6 | 1.1
J42 | 1.0 | 100 | 4.0 | 0.13 | 90.6 | 0.042 | 74.1 | 1.2
J43 | 2.0 | 100 | 4.0 | 0.07 | 90.9 | 0.041 | 74.7 | 1.4
J44 | 3.0 | 100 | 4.0 | 0.10 | 91.0 | 0.041 | 74.7 | 1.7
J45 | 0 | 80 | 4.0 | 0.15 | 89.8 | 0.046 | 71.6 | 1.3
J46 | 1.2 | 80 | 4.0 | 0.15 | 90.4 | 0.043 | 73.5 | 1.5
J47 | 0 | 100 | 4.0 | 0.20 | 90.5 | 0.043 | 73.5 | 1.7
J48 | 1.2 | 100 | 4.0 | 0.13 | 91.5 | 0.038 | 76.5 | 2.1

## Slide 25: Heritage Ranch CSD; Source Well 01; Jar Test 49 - 52 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | NaMnO4 mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J49 | 1.2 | 70 | 0.05 | 91.8 | 0.037 | 77.2 | 0.49
J50 | 0 | 70 | 0.05 | 90.9 | 0.041 | 74.7 | 0.80
J51 | 1.2 | 90 | 0.06 | 92.3 | 0.034 | 79.0 | 0.45
J52 | 0 | 90 | 0.05 | 92.2 | 0.035 | 78.4 | 0.51

## Slide 26: Heritage Ranch CSD; Source Well 01; Jar Test 53 - 60 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | NaMnO4 mg/L | Alum (dry) mg/L | 9890 mg/L | 186K pDADMAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J53 | 1.2 | 10 | 10 | - | 0.08 | 83.8 | 0.076 | 53.1 | 3.5
J54 | 1.2 | 40 | 10 | - | 0.12 | 88.3 | 0.053 | 67.3 | 1.3
J55 | 1.2 | 60 | 10 | - | 0.06 | 89.9 | 0.045 | 72.2 | 1.3
J56 | 1.2 | 80 | 10 | - | 0.15 | 90.8 | 0.041 | 74.7 | 1.5
J57 | 1.2 | 15 | - | 2 | 0.78 | 78.5 | 0.105 | 35.2 | 5.6
J58 | 1.2 | 40 | - | 2 | 0.18 | 85.5 | 0.067 | 58.6 | 2.6
J59 | 1.2 | 70 | - | 2 | 0.24 | 88.9 | 0.050 | 69.1 | 1.5
J60 | 1.2 | 100 | - | 2 | 0.09 | 90.9 | 0.041 | 74.7 | 1.5

## Slide 27: Heritage Ranch CSD; Source Well 01; Jar Test 61 - 68 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | NaMnO4 mg/L | Alum (dry) mg/L | 186K pDADMAC mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J61 | 1.2 | 15 | 6.0 | - | 0.05 | 83.0 | 0.080 | 50.6 | 4.9
J62 | 1.2 | 100 | 6.0 | - | 0.07 | 91.7 | 0.037 | 77.2 | 2.1
J63 | 1.2 | - | - | 70 | 0.06 | 90.8 | 0.041 | 74.7 | 0.83
J64 | 1.2 | - | - | 90 | 0.07 | 91.5 | 0.038 | 76.5 | 0.63
J65 | 1.2 | 15 | 6.0 | - | 0.09 | 82.5 | 0.083 | 48.8 | 3.6
J66 | 1.2 | 100 | 6.0 | - | 0.07 | 91.3 | 0.039 | 75.9 | 1.5
J67 | 1.2 | - | - | 70 | 0.05 | 90.1 | 0.045 | 72.2 | 0.41
J68 | 1.2 | - | - | 90 | 0.09 | 90.8 | 0.041 | 74.7 | 0.43

## Slide 28: Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals Alum

## Slide 29: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
20 mg/L Alum
Filtrate 0.63 NTU
UVT: 77.9%
UVA: 0.108/cm
UVA Reduction 34.6%
Settled: 6.3 NTU
30 mg/L Alum
Filtrate 0.81 NTU
UVT: 77.1%
UVA: 0.112/cm
UVA Reduction 30.9%
Settled: 6.1 NTU
40 mg/L Alum
Filtrate 0.72 NTU
UVT: 80.5%
UVA: 0.094/cm
UVA Reduction 42.0%
Settled: 5.6 NTU
50 mg/L Alum
Filtrate 0.12 NTU
UVT: 86.1%
UVA: 0.064/cm
UVA Reduction 60.5%
Settled: 2.5 NTU

## Slide 30: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 31: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L Alum
Filtrate 0.63 NTU
UVT: 77.9%
UVA: 0.108/cm
UVA Reduction 34.6%
Settled: 6.3 NTU
30 mg/L Alum
Filtrate 0.81 NTU
UVT: 77.1%
UVA: 0.112/cm
UVA Reduction 30.9%
Settled: 6.1 NTU
40 mg/L Alum
Filtrate 0.72 NTU
UVT: 80.5%
UVA: 0.094/cm
UVA Reduction 42.0%
Settled: 5.6 NTU
50 mg/L Alum
Filtrate 0.12 NTU
UVT: 86.1%
UVA: 0.064/cm
UVA Reduction 60.5%
Settled: 2.5 NTU

## Slide 32: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals Alum

## Slide 33: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
60 mg/L Alum
Filtrate 0.18 NTU
UVT: 87.1%
UVA: 0.058/cm
UVA Reduction 63.6%
Settled: 2.2 NTU
70 mg/L Alum
Filtrate 0.12 NTU
UVT: 87.7%
UVA: 0.053/cm
UVA Reduction 65.4%
Settled: 2.0 NTU
80 mg/L Alum
Filtrate 0.14 NTU
UVT: 88.3%
UVA: 0.052/cm
UVA Reduction 67.3%
Settled: 2.2 NTU
90 mg/L Alum
Filtrate 0.14 NTU
UVT: 89.3%
UVA: 0.046/cm
UVA Reduction 69.8%
Settled: 2.2 NTU

## Slide 34: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 35: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L Alum
Filtrate 0.18 NTU
UVT: 87.1%
UVA: 0.058/cm
UVA Reduction 63.6%
Settled: 2.2 NTU
70 mg/L Alum
Filtrate 0.12 NTU
UVT: 87.7%
UVA: 0.053/cm
UVA Reduction 65.4%
Settled: 2.0 NTU
80 mg/L Alum
Filtrate 0.14 NTU
UVT: 88.3%
UVA: 0.052/cm
UVA Reduction 67.3%
Settled: 2.2 NTU
90 mg/L Alum
Filtrate 0.14 NTU
UVT: 89.3%
UVA: 0.046/cm
UVA Reduction 69.8%
Settled: 2.2 NTU

## Slide 36: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals ProPac 9800

## Slide 37: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
60 mg/L 9800
Filtrate 0.06 NTU
UVT: 89.1%
UVA: 0.050/cm
UVA Reduction 69.1%
Settled: 1.7 NTU
70 mg/L 9800
Filtrate 0.05 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 71.6%
Settled: 1.2 NTU
80 mg/L 9800
Filtrate 0.05 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 72.8%
Settled: 1.2 NTU
90 mg/L 9800
Filtrate 0.07 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.4 NTU

## Slide 38: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 39: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.

## Slide 40: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals ProPac 9810

## Slide 41: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
60 mg/L 9810
Filtrate 0.05 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 0.72 NTU
70 mg/L 9810
Filtrate 0.12 NTU
UVT: 90.1%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 0.46 NTU
80 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 75.3%
Settled: 0.44 NTU
90 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 76.5%
Settled: 0.57 NTU

## Slide 42: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 43: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L 9810
Filtrate 0.05 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 0.72 NTU
70 mg/L 9810
Filtrate 0.12 NTU
UVT: 90.1%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 0.46 NTU
80 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 75.3%
Settled: 0.44 NTU
90 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 76.5%
Settled: 0.57 NTU

## Slide 44: Jars 17-20 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals Alum

## Slide 45: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
100 mg/L Alum
Filtrate 0.06 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 75.3%
Settled: 1.3 NTU
110 mg/L Alum
Filtrate 0.07 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 75.3%
Settled: 1.9 NTU
120 mg/L Alum
Filtrate 0.07 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 75.3%
Settled: 2.6 NTU
130 mg/L Alum
Filtrate 0.07 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 75.9%
Settled: 2.1 NTU

## Slide 46: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 47: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
100 mg/L Alum
Filtrate 0.06 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 75.3%
Settled: 1.3 NTU
110 mg/L Alum
Filtrate 0.07 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 75.3%
Settled: 1.9 NTU
120 mg/L Alum
Filtrate 0.07 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 75.3%
Settled: 2.6 NTU
130 mg/L Alum
Filtrate 0.07 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 75.9%
Settled: 2.1 NTU

## Slide 48: Jars 21-24 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals Alum 186K pDADMAC

## Slide 49: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
70 mg/L Alum
3.0 mg/L 186K pDADMAC
Filtrate 0.10 NTU
UVT: 89.1%
UVA: 0.049/cm
UVA Reduction 69.8%
Settled: 1.4 NTU
70 mg/L Alum
3.0 mg/L 186K pDADMAC
Filtrate 0.06 NTU
UVT: 89.5%
UVA: 0.047/cm
UVA Reduction 71.0%
Settled: 1.5 NTU
70 mg/L Alum
3.0 mg/L 186K pDADMAC
Filtrate 0.10 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.5 NTU
70 mg/L Alum
3.0 mg/L 186K pDADMAC
Filtrate 0.10 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 72.8%
Settled: 1.6 NTU

## Slide 50: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 51: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
70 mg/L Alum
3.0 mg/L 186K pDADMAC
Filtrate 0.10 NTU
UVT: 89.1%
UVA: 0.049/cm
UVA Reduction 69.8%
Settled: 1.4 NTU
70 mg/L Alum
3.0 mg/L 186K pDADMAC
Filtrate 0.06 NTU
UVT: 89.5%
UVA: 0.047/cm
UVA Reduction 71.0%
Settled: 1.5 NTU
70 mg/L Alum
3.0 mg/L 186K pDADMAC
Filtrate 0.10 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.5 NTU
70 mg/L Alum
3.0 mg/L 186K pDADMAC
Filtrate 0.10 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 72.8%
Settled: 1.6 NTU

## Slide 52: Jars 25-28 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals Alum

## Slide 53: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
0 mg/L PAC
100 mg/L Alum
Filtrate 0.16 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 69.8%
Settled: 1.7 NTU
5 mg/L PAC
100 mg/L Alum
Filtrate 0.43 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction 67.9%
Settled: 1.6 NTU
10 mg/L PAC
100 mg/L Alum
Filtrate 0.26 NTU
UVT: 89.5%
UVA: 0.048/cm
UVA Reduction 70.4%
Settled: 2.0 NTU
15 mg/L PAC
100 mg/L Alum
Filtrate 0.22 NTU
UVT: 89.7%
UVA: 0.047/cm
UVA Reduction 71.0%
Settled: 1.1 NTU

## Slide 54: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 55: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
100 mg/L Alum
Filtrate 0.16 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 69.8%
Settled: 1.7 NTU
5 mg/L PAC
100 mg/L Alum
Filtrate 0.43 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction 67.9%
Settled: 1.6 NTU
10 mg/L PAC
100 mg/L Alum
Filtrate 0.26 NTU
UVT: 89.5%
UVA: 0.048/cm
UVA Reduction 70.4%
Settled: 2.0 NTU
15 mg/L PAC
100 mg/L Alum
Filtrate 0.22 NTU
UVT: 89.7%
UVA: 0.047/cm
UVA Reduction 71.0%
Settled: 1.1 NTU

## Slide 56: Jars 29-32 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals PAC Alum 186K pDADMAC

## Slide 57: Jars 29-32: End of 5-minute flocculation (30 RPM) duration.
0 mg/L PAC
100 mg/L Alum
3.0 mg/L 186K
Filtrate 0.13 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 1.9 NTU
5 mg/L PAC
100 mg/L Alum
3.0 mg/L 186K
Filtrate 0.09 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 74.1%
Settled: 1.7 NTU
10 mg/L PAC
100 mg/L Alum
3.0 mg/L 186K
Filtrate 0.05 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 2.1 NTU
15 mg/L PAC
100 mg/L Alum
3.0 mg/L 186K
Filtrate 0.04 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 75.9%
Settled: 1.7 NTU

## Slide 58: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 59: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
100 mg/L Alum
3.0 mg/L 186K
Filtrate 0.13 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 1.9 NTU
5 mg/L PAC
100 mg/L Alum
3.0 mg/L 186K
Filtrate 0.09 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 74.1%
Settled: 1.7 NTU
10 mg/L PAC
100 mg/L Alum
3.0 mg/L 186K
Filtrate 0.05 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 2.1 NTU
15 mg/L PAC
100 mg/L Alum
3.0 mg/L 186K
Filtrate 0.04 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 75.9%
Settled: 1.7 NTU

## Slide 60: Jars 33-36 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals PAC ProPac 9810

## Slide 61: Jars 33-36: End of 5-minute flocculation (30 RPM) duration.
0 mg/L PAC
80 mg/L 9810
Filtrate 0.13 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 71.6%
Settled: 1.1 NTU
5 mg/L PAC
80 mg/L 9810
Filtrate 0.24 NTU
UVT: 88.9%
UVA: 0.056/cm
UVA Reduction 65.4%
Settled: 1.4 NTU
10 mg/L PAC
80 mg/L 9810
Filtrate 0.07 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.4 NTU
15 mg/L PAC
80 mg/L 9810
Filtrate 0.09 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.3 NTU

## Slide 62: Jars 33-36: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 63: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
80 mg/L 9810
Filtrate 0.13 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 71.6%
Settled: 1.1 NTU
5 mg/L PAC
80 mg/L 9810
Filtrate 0.24 NTU
UVT: 88.9%
UVA: 0.056/cm
UVA Reduction 65.4%
Settled: 1.4 NTU
10 mg/L PAC
80 mg/L 9810
Filtrate 0.07 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.4 NTU
15 mg/L PAC
80 mg/L 9810
Filtrate 0.09 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.3 NTU

## Slide 64: Jars 37-40 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals 961

## Slide 65: Jars 37-40: End of 5-minute flocculation (30 RPM) duration.
60 mg/L 961
Filtrate 0.06 NTU
UVT: 88.7%
UVA: 0.051/cm
UVA Reduction 88.7%
Settled: 3.6 NTU
70 mg/L 961
Filtrate 0.09 NTU
UVT: 89.0%
UVA: 0.050/cm
UVA Reduction 89.0%
Settled: 6.6 NTU
80 mg/L 961
Filtrate 0.36 NTU
UVT: 86.7%
UVA: 0.062/cm
UVA Reduction 86.7%
Settled: 6.3 NTU
90 mg/L 961
Filtrate 1.23 NTU
UVT: 80.0%
UVA: 0.097/cm
UVA Reduction 80.0%
Settled: 6.3 NTU

## Slide 66: Jars 37-40: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 67: Jars 37-40: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L 961
Filtrate 0.06 NTU
UVT: 88.7%
UVA: 0.051/cm
UVA Reduction 88.7%
Settled: 3.6 NTU
70 mg/L 961
Filtrate 0.09 NTU
UVT: 89.0%
UVA: 0.050/cm
UVA Reduction 89.0%
Settled: 6.6 NTU
80 mg/L 961
Filtrate 0.36 NTU
UVT: 86.7%
UVA: 0.062/cm
UVA Reduction 86.7%
Settled: 6.3 NTU
90 mg/L 961
Filtrate 1.23 NTU
UVT: 80.0%
UVA: 0.097/cm
UVA Reduction 80.0%
Settled: 6.3 NTU

## Slide 68: Jars 41-44 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals NaMnO4 Alum 186K pDADMAC

## Slide 69: Jars 41-44: End of 5-minute flocculation (30 RPM) duration.
0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.06 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 71.6%
Settled: 1.1 NTU
1.0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.13 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 74.1%
Settled: 1.2 NTU
2.0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.07 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 1.4 NTU
3.0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.10 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 1.7 NTU

## Slide 70: Jars 41-44: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 71: Jars 41-44: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.06 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 71.6%
Settled: 1.1 NTU
1.0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.13 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 74.1%
Settled: 1.2 NTU
2.0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.07 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 1.4 NTU
3.0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.10 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 1.7 NTU

## Slide 72: Jars 45-48 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals NaMnO4 Alum 186K pDADMAC

## Slide 73: Jars 45-48: End of 5-minute flocculation (30 RPM) duration.
0 mg/L NaMnO4
80 mg/L Alum
4.0 mg/L 186K
Filtrate 0.15 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 71.6%
Settled: 1.3 NTU
1.2 mg/L NaMnO4
80 mg/L Alum
4.0 mg/L 186K
Filtrate 0.15 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.5 NTU
0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.20 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.7 NTU
1.2 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.13 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 76.5%
Settled: 2.1 NTU

## Slide 74: Jars 45-48: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 75: Jars 45-48: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaMnO4
80 mg/L Alum
4.0 mg/L 186K
Filtrate 0.15 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 71.6%
Settled: 1.3 NTU
1.2 mg/L NaMnO4
80 mg/L Alum
4.0 mg/L 186K
Filtrate 0.15 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.5 NTU
0 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.20 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 73.5%
Settled: 1.7 NTU
1.2 mg/L NaMnO4
100 mg/L Alum
4.0 mg/L 186K
Filtrate 0.13 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 76.5%
Settled: 2.1 NTU

## Slide 76: Jars 49-52 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals NaMnO4 ProPac 9810

## Slide 77: Jars 49-52: End of 5-minute flocculation (30 RPM) duration.
1.2 mg/L NaMnO4
70 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction 77.2%
Settled: 0.49 NTU
0 mg/L NaMnO4
70 mg/L 9810
Filtrate 0.05 NTU
UVT: 90.9%
UVA: 0.037/cm
UVA Reduction 74.7%
Settled: 0.80 NTU
1.2 mg/L NaMnO4
90 mg/L 9810
Filtrate 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 79.0%
Settled: 0.45 NTU
0 mg/L NaMnO4
90 mg/L 9810
Filtrate 0.05 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 78.4%
Settled: 0.51 NTU

## Slide 78: Jars 49-52: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 79: Jars 49-52: After 25-minutes of settling, settled water turbidity is taken.
1.2 mg/L NaMnO4
70 mg/L 9810
Filtrate 0.05 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction 77.2%
Settled: 0.49 NTU
0 mg/L NaMnO4
70 mg/L 9810
Filtrate 0.05 NTU
UVT: 90.9%
UVA: 0.037/cm
UVA Reduction 74.7%
Settled: 0.80 NTU
1.2 mg/L NaMnO4
90 mg/L 9810
Filtrate 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 79.0%
Settled: 0.45 NTU
0 mg/L NaMnO4
90 mg/L 9810
Filtrate 0.05 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 78.4%
Settled: 0.51 NTU

## Slide 80: Jars 53-56 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals NaMnO4 Alum ProPac 9890

## Slide 81: Jars 53-56: End of 5-minute flocculation (30 RPM) duration.
1.2 mg/L NaMnO4
10 mg/L Alum
10 mg/L 9890
Filtrate 0.08 NTU
UVT: 83.8%
UVA: 0.076/cm
UVA Reduction 53.1%
Settled: 3.5 NTU
1.2 mg/L NaMnO4
40 mg/L Alum
10 mg/L 9890
Filtrate 0.12 NTU
UVT: 88.3%
UVA: 0.053/cm
UVA Reduction 67.3%
Settled: 1.3 NTU
1.2 mg/L NaMnO4
60 mg/L Alum
10 mg/L 9890
Filtrate 0.06 NTU
UVT: 89.9%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 1.3 NTU
1.2 mg/L NaMnO4
80 mg/L Alum
10 mg/L 9890
Filtrate 0.15 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 1.5 NTU

## Slide 82: Jars 53-56: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 83: Jars 53-56: After 25-minutes of settling, settled water turbidity is taken.
1.2 mg/L NaMnO4
10 mg/L Alum
10 mg/L 9890
Filtrate 0.08 NTU
UVT: 83.8%
UVA: 0.076/cm
UVA Reduction 53.1%
Settled: 3.5 NTU
1.2 mg/L NaMnO4
40 mg/L Alum
10 mg/L 9890
Filtrate 0.12 NTU
UVT: 88.3%
UVA: 0.053/cm
UVA Reduction 67.3%
Settled: 1.3 NTU
1.2 mg/L NaMnO4
60 mg/L Alum
10 mg/L 9890
Filtrate 0.06 NTU
UVT: 89.9%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 1.3 NTU
1.2 mg/L NaMnO4
80 mg/L Alum
10 mg/L 9890
Filtrate 0.15 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 1.5 NTU

## Slide 84: Jars 57-60 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals NaMnO4 Alum 186K pDADMAC

## Slide 85: Jars 57-60: End of 5-minute flocculation (30 RPM) duration.
1.2 mg/L NaMnO4
15 mg/L Alum
2.0 mg/L 186K
Filtrate 0.78 NTU
UVT: 78.5%
UVA: 0.105/cm
UVA Reduction 35.2%
Settled: 5.6 NTU
1.2 mg/L NaMnO4
40 mg/L Alum
2.0 mg/L 186K
Filtrate 0.18 NTU
UVT: 85.5%
UVA: 0.067/cm
UVA Reduction 58.6%
Settled: 2.6 NTU
1.2 mg/L NaMnO4
70 mg/L Alum
2.0 mg/L 186K
Filtrate 0.24 NTU
UVT: 89.9%
UVA: 0.050/cm
UVA Reduction 69.1%
Settled: 1.5 NTU
1.2 mg/L NaMnO4
100 mg/L Alum
2.0 mg/L 186K
Filtrate 0.09 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 1.5 NTU

## Slide 86: Jars 57-60: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 87: Jars 57-60: After 25-minutes of settling, settled water turbidity is taken.
1.2 mg/L NaMnO4
15 mg/L Alum
2.0 mg/L 186K
Filtrate 0.78 NTU
UVT: 78.5%
UVA: 0.105/cm
UVA Reduction 35.2%
Settled: 5.6 NTU
1.2 mg/L NaMnO4
40 mg/L Alum
2.0 mg/L 186K
Filtrate 0.18 NTU
UVT: 85.5%
UVA: 0.067/cm
UVA Reduction 58.6%
Settled: 2.6 NTU
1.2 mg/L NaMnO4
70 mg/L Alum
2.0 mg/L 186K
Filtrate 0.24 NTU
UVT: 89.9%
UVA: 0.050/cm
UVA Reduction 69.1%
Settled: 1.5 NTU
1.2 mg/L NaMnO4
100 mg/L Alum
2.0 mg/L 186K
Filtrate 0.09 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 1.5 NTU

## Slide 88: Jars 61-64 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals NaMnO4 Alum 186K pDADMAC ProPac 9810

## Slide 89: Jars 61-64: End of 5-minute flocculation (30 RPM) duration.
1.2 mg/L NaMnO4
15 mg/L Alum
6.0 mg/L 186K
Filtrate 0.05 NTU
UVT: 83.0%
UVA: 0.080/cm
UVA Reduction 50.6%
Settled: 4.9 NTU
1.2 mg/L NaMnO4
100 mg/L Alum
6.0 mg/L 186K
Filtrate 0.07 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 77.2%
Settled: 2.1 NTU
1.2 mg/L NaMnO4
70 mg/L 9810
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 0.83 NTU
1.2 mg/L NaMnO4
90 mg/L 9810
Filtrate 0.07 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 76.5%
Settled: 0.63 NTU

## Slide 90: Jars 61-64: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 91: Jars 61-64: After 25-minutes of settling, settled water turbidity is taken.
1.2 mg/L NaMnO4
15 mg/L Alum
6.0 mg/L 186K
Filtrate 0.05 NTU
UVT: 83.0%
UVA: 0.080/cm
UVA Reduction 50.6%
Settled: 4.9 NTU
1.2 mg/L NaMnO4
100 mg/L Alum
2.0 mg/L 186K
Filtrate 0.07 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 77.2%
Settled: 2.1 NTU
1.2 mg/L NaMnO4
70 mg/L 9810
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 0.83 NTU
1.2 mg/L NaMnO4
90 mg/L 9810
Filtrate 0.07 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 76.5%
Settled: 0.63 NTU

## Slide 92: Jars 65-68 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Chemicals NaMnO4 Alum 186K pDADMAC 9810

## Slide 93: Jars 65-68: End of 5-minute flocculation (30 RPM) duration.
1.2 mg/L NaMnO4
15 mg/L Alum
6.0 mg/L 186K
Filtrate 0.09 NTU
UVT: 82.5%
UVA: 0.083/cm
UVA Reduction 48.8%
Settled: 3.6 NTU
1.2 mg/L NaMnO4
100 mg/L Alum
6.0 mg/L 186K
Filtrate 0.07 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 75.9%
Settled: 1.5 NTU
1.2 mg/L NaMnO4
70 mg/L 9810
Filtrate 0.05 NTU
UVT: 90.1%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 0.41 NTU
1.2 mg/L NaMnO4
90 mg/L 9810
Filtrate 0.09 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 0.43 NTU

## Slide 94: Jars 65-68: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 95: Jars 65-68: After 25-minutes of settling, settled water turbidity is taken.
1.2 mg/L NaMnO4
15 mg/L Alum
6.0 mg/L 186K
Filtrate 0.09 NTU
UVT: 82.5%
UVA: 0.083/cm
UVA Reduction 48.8%
Settled: 3.6 NTU
1.2 mg/L NaMnO4
100 mg/L Alum
6.0 mg/L 186K
Filtrate 0.07 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 75.9%
Settled: 1.5 NTU
1.2 mg/L NaMnO4
70 mg/L 9810
Filtrate 0.05 NTU
UVT: 90.1%
UVA: 0.045/cm
UVA Reduction 72.2%
Settled: 0.41 NTU
1.2 mg/L NaMnO4
90 mg/L 9810
Filtrate 0.09 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 74.7%
Settled: 0.43 NTU

## Slide 96: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 97: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 98: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 99: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 100: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 101: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732