## Slide 1: Gibson Canyon WTP Solano Irrigation District Vacaville County, CA Contact Time (t10) Tracer Study May 8, 2017
by Guy Schott, P.E.
Amy Little, P.E.
Water Resources Control Board,
Division of Drinking Water
Guy.schott@waterboards.ca.gov
707-576-2732

## Slide 2
Chlorine Contact Tank - Clearwell
Clearwell volume/ft: 2,844 gal/ft
Working volume during tracer study: 34,000 gallons
Inlet 2.8-ft off bottom angled 30o up
Outlet 2-in off bottom
L:W ratio: 11
Has spray aeration for TTHM reduction pumped from outlet pipe back into tank top in last channel.

## Slide 3: Final Results
Test Date: May 8, 2017
Test by: Water Resources Control Board, Division of Drinking Water
Tracer Test Method: Modified Step-Dose using Fluoride
Clearwell Diameter: 22-ft
Clearwell Volume/Ft: 2,844 gal/ft
Number of Baffles: 2
Clearwell Flow (inlet/outlet): 400 gpm
Clearwell Operating Water Level: 12 feet
Clearwell Operating Volume: 34,000 gallons
HRT: 85 minutes
t10: 31.3 minutes
L:W Ratio: 11
Baffling Factor: 0.37 (t10/HRT)

## Slide 4: Tracer Study – Overview 1
A tracer study was conducted at the Gibson Canyon WTP to determine the “t10” disinfection contact time and baffling factor for the 40,000 gallon max capacity clearwell with two baffles. The “t10” value is the time is takes for 10% of the added tracer mass to exit the reactor. The baffling factor is t10/HRT where HRT is the hydraulic residence time of the clearwell during the time of the tracer study.

## Slide 5: Tracer Study – Overview 2
Tracer Method: Modified Step-Dose
Injection Point: Pipeline inlet to Clearwell
Sample Points: Inlet/outlet of Clearwell
Tracer Analysis: Ion Selective Fluoride Probe
Sampler: Amy Little
Analysis by: Guy Schott

## Slide 6: Tracer Material Overview
Tracer Material: Hydrofluorosillicic Acid (H2SiF6)
Tracer Bulk Density: 10.3 lbs/gal
Tracer Product Strength: 28% as H2SiF6
Molecular Weight: 144.09 g/mole (H2SiF6)
Fluoride Concentration: 79.11% (144 g/mole)
H2SiF6 Tracer Feed Rate: ~21 mL/min
Flow: 400 gpm
Tracer Dose: 3.9 mg/L as F
Method of Injection: Steady-State

## Slide 7: Tracer Field Results
Flow: 400 gpm; 40,000 gallon baffled Clearwell
HRT: 85 minutes
Tracer Dose– 3.9 mg/L as F
t10: 31.3 minutes
Working volume: 32,000 gallons @ 12 ft operating level
Calculated baffling factor: 0.37 t10/HRT
L:W ratio: 11

## Slide 8
Working Volume: 34,000 gallons
Average Flow: 400 gpm
Clearwell Water Level: 12 ft
Total Baffles: 2
HRT: 85 minutes
t10: 31.3 minutes
Baffling factor 0.37 (t10/HRT)

## Slide 9
Clearwell and Effluent Pumps
Tracer Sample Point (discharge side of effluent pumps)

## Slide 10
Inlet Sample Point before Clearwell
To Verify Tracer Dosage