## Slide 1: Jar Testing Confidence in Results for Plant Application CA-NV AWWA Water Conference of the West, San Diego, CA
by Guy Schott, P.E. April 7, 2026
Drought
Algal Bloom (Microcystin)
Rain Event
Algal Bloom (Lyngbya)

## Slide 2: Presentation Overview
The importance of jar testing and outcomes
Lab Equipment/Materials
Analysis (Filterability, UVT/UVA & Settleability)
Procedures
Case/Application Study
Training Video – Jar Testing Done Right

## Slide 3: Why Jar Test?
When there is a change in source water quality that can impact
  Filtration process
  Disinfection by-product formations
Evaluate
  pre-oxidants (chlorine, KMnO4, ozone)
  pH adjustment
  powder activated carbon
  other coagulants and organic polymers
To practice

## Slide 4: Jar Testing & Analysis – What’s Important
The chemistry that results in the best
Filterability (floc strength, turbidity, and head loss)
Dissolved organic carbon reduction (UVA surrogate)
Settleability (turbidity)
Confidence in your jar testing results
Fast, simple, and effective

## Slide 5: Lab
UVA/%UVT
Turbidity
Cuvettes
Stock
Solutions
Pipettes
100-1000 uL
0.5-5 mL
Filters
(1.2 um absolute
Isopore polycarbonate
membrane)
Luer-Lock Syringes (30 cc)
4-Jar Tester

## Slide 6: 1. Filterability Analysis
Evaluate which chemicals and dose provide the best filtrate NTU (<0.1 NTU)
1.2 um absolute Isopore polycarbonate membrane
Weak floc - increase filtrate turbidity
Strong floc - decrease in filtrate turbidity
Samples are collected at end of flocculation period (0-5 minutes)
Notes: Discuss if your difference pore size

## Slide 7: Filterability Sensitivity Performance Analysis – Plant dose (Alum: 35 mg/L, pDADMAC: 6.0 mg/L product)
Floc
Strength
Filtrate
NTU
pDADMAC
Solution
mg/L
Alum
(dry)
mg/L
Jar#
Very Weak
1.06
0
35
J1
Very Weak
0.66
0
45
J2
Weak
0.27
0
55
J3
Weak
0.26
0
65
J4
Good
0.10
6.0
35
J5
Strong
0.05
6.0
45
J6
Strong
0.04
6.0
55
J7
Strong
0.05
6.0
65
J8

## Slide 8: Use the Correct Specified Filter
1.2 um Polycarbonate Filter
Correct filter for Jar Testing
1.2 um Polyethersulfone Filter
Incorrect filter for Jar Testing

## Slide 9: Specified Filter Material/Size must be used.
For filterability analysis, use Isopore Membrane Filter, 1.2 um absolute pore size, Φ= 25 mm , thickness: 24 um, hydrophilic polycarbonate membrane (part #: RTTP02500, Sigma-Aldrich)
*Note: Laboratory Charged Analyzer (LCA) results: 3.9 mg/L as coagulant product
Filtrate NTU
(Polycarbonate)
1.2 um Membrane
Specified Filter
Filtrate NTU
(Polyethersulfone)
1.2 um Membrane
Incorrect Filter
Blend of
*ACH/pDADMAC
mg/L
Jar #
0.13
0.04
3.0
J1
0.06
0.04
3.5
J2
0.04
0.04
4.0
J3
0.05
0.04
5.5
J4
0.08
0.04
6.0
J5
0.23
0.05
6.5
J6

## Slide 10: 2. Filtrate UV-Absorption (UVA) Analysis
Surrogate for dissolved organic carbon (DOC)
Compare %UVA reduction between jars
% UVA Reduction = (Source UVA – Filtrate UVA)/(Source UVA)*100%
Systems with DPB issues, UVA measurements are critical for determining optimum coagulant and dose
Notes: Discuss if your difference pore size

## Slide 11: 2. Filtrate UV-Absorption (UVA) Analysis –Ex
Note: There is an additional 35% reduction in UVA from Jar 1 to 2.
HAA5
ug/L
TTHM
ug/L
Settled
NTU
%UVA
Reduction
Filtrate
UVA/cm
Filtrate
%UVT
Filtrate
NTU
Jar
63
90
2.0
65.9
0.046
89.9
0.04
Plant
Dose
40
59
2.0
77.8
0.030
93.2
0.04
Optimum
Dose
Notes: Discuss if your difference pore size

## Slide 12: 3. Settleability Analysis
Relative performance measurement between jars based on coagulant type, dose and flocculation duration
Samples are collected 25 minutes from the end of the flocculation period for a 4-jar tester
Note: Settleability has no supporting data on filterability and UVA reduction

## Slide 13: Jar Testing Procedures and Analysis
Jar Testing 5.5 minutes | 
1. Flash Mix 200 RPM (20-30 sec) | 2. Flocculation 20-30 RPM (5 min)
*Note: Floc duration longer than 5 minutes has no significant impact on filterability and filtrate UVA results.
35 minutes or less complete 4-jar testing and analysis
Analysis 20 - 25 minutes | 
3. Filterability & Filtrate %UVT/UVA (5 min/jar = 20 min) | 4. Settleability (5 min)

## Slide 14: End of 5-minute flocculation (30 RPM) duration.

## Slide 15: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 16: Syringing
Filterability (20-25 mL syringed)

## Slide 17: Filterability and UVT/UVA Analysis (5 min/Jar)
1.
2.
3.
4.
Flocculated water is pushed through a 1.2 um absolute polycarbonate membrane (drip-rate) into cuvette
Measured filtrate turbidity (several readings until stable) and record
Transfer water from cuvette to UVT/UVA cuvette
Measure UVT/UVA and record

## Slide 18: Settleability Sampling

## Slide 19: Kenya Tenwek Hospital Surface Water Treatment Plant
Mission:
Plant Optimization & Operator Training
Onsite: April/May 2022
Case Study:

## Slide 20: Case 1: Kenya -Tenwek Hospital Surface Water Treatment Plant
Surface Water Treatment Plant
(29.17 m3/hr., 128 gpm, 700 m3/day, 184,940 gal/day)
Gravity
Chemical
Feeders
Clarifier
& Filter
Clearwell
Booster
Pump
Bld

## Slide 21: River Mara
Source Water
  River Mara
  Alkalinity: 12 mg/L CaCO3
  pH: 6s
  Turbidity: 300 – 800 NTU
  Rain every afternoon

## Slide 22: Case 1. Upon arrival (April 2022) at Tenwek Hospital – New Surface Water Treatment Plant
  Source Alkalinity: 12 mg/L CaCO3
  Chemical added at source: Alum/Soda Ash
  Clearwell: Calcium Hypochlorite
  Plant operating filtrate turbidity: >1 - 5 NTUs
  Filter backwash frequency: once every 8 hours
  Kenya’s turbidity performance standard: <=5 NTUs

## Slide 23: Kenya - Tenwek
Chemical Storage/
Gravity feeders
CFI (composite filtration unit)
100 m3 Clearwell
Treated/Backwash
Pump Building
Sludge Drying
Beds

## Slide 24: Clarifier/Filter
Sand
Filter

## Slide 25: Sand Filter Dia.: 8.86-ft Area: 78.47 ft2

## Slide 26: Jar Testing - Results
Soda Ash (Na2CO3) had negative impact on filterability
  Moved Na2CO3 to post filtration
  Optimized Alum dose via jar testing
  Results:
    Filtrate turbidity <0.1 NTU
    Filtrate UVA: 0.008/cm
    Filtrate UVT: 98%
    Filter backwash every 24 hours

## Slide 27: Laboratory
https://kewi.go.ke/
Victor Siele (operator)

## Slide 28: Operators learning jar testing

## Slide 29: Victor with NTU

## Slide 30: Thank you for attending! Contact and Links
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Jar Test Results/Procedures for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right video training https://youtu.be/aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732