## Inactive Project List
Project Number | System Number | Borrower Name/System Name | Project Name | Project Description | Project Category | System Type | Problem | Costs | Connections | Population | District | County | Region | List Year
5510013-005 | 5510013 | TUD - Columbia Water System | Shaws Flat Pipeline Extension | CONSTRUCT A WATER MAIN EXTENSION FROM THE COLUMBIA SYSTEM INTO THE SHAWS FLAT COMMUNITY. | B | C | THE SHAWS FLAT AREA HAS NUMEROUS FAILING SEPTIC TANK SYSTEMS THAT HAVE CAUSED MICROBIAL CONTAMINATION OF THE LOCAL WELLS. | 574000 | 1548 | 3646 | 11 | Tuolumne | III | 1998
0011123-001 | 0011123 | T.U.D. Mountian Boy Ditch Conveyance | Mountain Boy Road Conveyance Project | CONSTRUCT A WATER SYSTEM WITH A WATER TREATMENT PLANT, STORAGE, AND PIPELINES; OR EXTEND WATER LINES FROM THE BIG HILL WATER SYSTEM TO SERVE THE DITCH CUSTOMERS. | B | U | INDIVIDUAL DITCH CUSTOMERS USING UNTREATED DITCH WATER SUPPLIED BY TUD. | 364880 | 15 | 30 | 11 | Tuolumne | III | 1998
0011120-001 | 0011120 | T.U.D. Ditch Conveyance Conversion | TUD-DITCH CONVEYANCE CONVERSION | INSTALL THREE WATERING STATIONS, TWO WATER MAIN EXTENSIONS, SIX WATER SERVICE EXTENSIONS, AND UP TO 20 WELLS. | B | U | INDIVIDUAL DITCH CUSTOMERS USING UNTREATED DITCH WATER SUPPLIED BY TUD. | 1200000 | 15 | 180 | 11 | Tuolumne | III | 1998
4210013-001 | 4210013 | SOLVANG WATER DEPARTMENT | SWTR Compliance | Install 1.85 MGD fitlration and disinfection TP to comply with the SWTR. | C | C | Sources are subject to SWTR compliance and are not filtered. | 1980300 | 1916 | 5383 | 06 | Santa Barbara | IV | 1998
1206008-001 | 1206008 | Mattole Triple Junction High School | SWTR Compliance | Surface water treatment rule compliance. | D | P | Turbidity failures 8 months out of the year. This system uses a surface water source. The Mattole river reaches turbidities of 800+ NTU. Lack of analyzers on site makes it difficult to design or plan a solution | 225000 | 1 | 60 | 01 | Humboldt | I | 2002
1910067-037 | 1910067 | LOS ANGELES-CITY, DEPT. OF WATER & POWER | City T/L South Unit 6 | Replaces 1914 Riveted Steel Pipe. Primary source to eastern portion of San Fernando Valley and to Franklin, Hollywood, and Silver Lake service areas. Increases reliability. Title of Regulation: Surface Water Treatment Rule. City Trunk Line South (CTLS) Unit 6 is one of 6 units of the CTLS, which is needed to replace the existing CTLS. CTLS 6 is 1,630 feet of 60" diameter welded steel pipe. The project route is along Coldwater Canyone Blvd. between Avenida del Sol to the North Portal of the Franklin Tunnel. This project includes the installation of the following: 6 butterfly valves, 1 flowmeter, 1 vault, and 1 jacks/tunnels. The jacks/tunnels account for 1,450 feet of the total project length. This project includes two connections, one to the Coldwater Canyon Pump Station and another to the North Portal of the Franklin tunnel. | D | C | Replaces 1914 Riveted Steel Pipe. Primary sorce to eastern portion of San Fernando Valley and to Franklin, Hollywood, and Silver Lake service areas. Increases reliability. Title of Regulation: Surface Water Treatment Rule. This is necessary for reliability and operational flexibility. | 18900000 | 686422 | 4071873 | 15 | Los Angeles | IV | 2009
1206002-003 | 1206002 | Palomino Estates M.W.C. | Replace in-line filtration system with direct filtration system | Planning,Engineering, design and construction of approved technology to meet EPA's Long Term Enhance Surface Water Treatment Rules. | D | C | Current in-line filtration system may not meet EPA's Long Term 1 and 2 Enhanced Surface Water Treatment Rules. May need upgrading to an approved technology, such as, Direct Filtration. | 250000 | 19 | 64 | 01 | Humboldt | I | 2013
1300572-001P | 1300572 | VALLEY MOBILE PARK | Planning | Construct a new surface water treatment plant. | D | C | Surface water treatment plant does not meet SWTR Regulations of treatment technique. | 170000 | 22 | 70 | 14 | Imperial | V | 1999
4900570-004 | 4900570 | Palomino Lakes Mutual Water Co. | Well replacement to overcome the direct influence of surface water | Please note that "consolidation" is not an option. The closest public water system is five miles away. There are no private systems with the ability to help within that same five miles.The problem of the well being substandard has been known for some time. The Palomino Lakes Mutual Water Company (PLMWC) Board began negotiations with vineyard owner (where the present well is located) some time ago. To date it has been an unsuccessful process however very recently the talks have become considerably more productive. Based on the progress there appears a successful resolution may be at hand. Additionally the Board is exploring a possible site on the adjacent parcel that was actually suggested by the reluctant vineyard owner while he negotiated.The solution is a new, deeper well, closer to the Russian River, where sufficient depth is available to allow the well to meet sanitation standards while being far enough away to minimize turbidity problems. All of the expected well drilling, casing, proving, drilling waste control and removal, etc expenses will be required.Also required are the usual support items including a pump, controls, electrical service, water treatment equipment and structure, monitoring equipment, underground piping to connect into the existing water main, etc. as well as additional access road and fencing.Since certain aspects of this project are givens, regardless of well location, the design concepts, the equipment evaluations, the construction techniques, the permitting and the various sanitation and/or filtration concepts are being studied, evaluated and costed. Additionally there will be legal fees, engineering fees, surveyor fees, hydrogeologist fees and landowners easement fees.It should be noted here that while a deeper well, with a deeper surface seal has traditionally solved the GWUDI problem it is conceivable something unforeseen could increase the complexity of the treatment process.The PLMWC Board of Directors is currently devloping an action plan for the Department's approval and until a plan is approved a final budget is not possible to creat. | D | C | On May 10, 2011 the Department of Public Health (Department) Drinking Water Field Operations staff inspected the Palomino Lakes Mutual Water Company (PLMWC) facilities. This inspection, and test results from early 2011, caused the Department to notify the PLMWC the well was not at Department standards.The PLMWC immediately modified the water treatment procedure to meet a 3-log inactivation of Giardia and a 4-log inactivation of virus through higher disinfection. This action was reported to the Department during a June 17, 2011 meeting in Santa Rosa between the Department, the PLMWC system operator and the PLMWC Board of Directors.On June 23, 2011 Janice M. Oakley, P.E., Sonoma County Engineer for the Drinking Water Field Operations Branch based in Santa Rosa, formally notified the PLMWC the system's well was being reclassified as "...a groundwater under the direct influence (GWUDI) of surface water". The Surface Water Treatment Rule, sections 64650-64666 of the CCR, was specifically cited.By instituting the higher disinfection rate and logging data on regular basis a "boil water" has not been necessary and all water users are being updated as needed. The problem stems from the well depth of only twenty-four feet and the surface seal only being four feet. Additionally this well is in a vineyard where the surface waters may contain farming chemicals as well as wild animal contaminants. | 500000 | 110 | 340 | 18 | Sonoma | II | 2012
0910018-001 | 0910018 | El Dorado ID - Outingdale | EID Outingdale consolidation | consolidate with EID Main system; 5 miles of 10 inch water main | D | C | SWTR violation | 5500000 | 189 | 497 | 09 | El Dorado | I | 2002
2310007-006 | 2310007 | North Gualala Water Company | Water Source & Storage Construction | Following a planning study, NGWC plans to develop recommendations that address source capacity deficiencies. Our current source deficiency amounts to 250 gpm (or ac-feet). Our construction project would allow NGWC to comply with State Water Resources WR 2001-14 requirements. Build a reservior and water treatment plant to process the reservior held water. Water storage issues could be solved with enlarged tank farms to increase distribution. | E | C | By Order 2001-14, the State Water Resources Control Board (Board) requires our community to only operate two wells if minimum bypass requirements are met. These two wells account for 85% of our source production during maximum day demand. By Order WR 2001-14, our well field production capacity has been reduced from 250 gpm to 0 gpm, while maintaining our minimum bypass requirements. The elimination of the well field reduces our overall system capacity during maximum day demand conditions. The Calif. Code of Regulations requires our source capacity to, at minimum, meet our maximum day demand. As a result of Order 2001-14, our reduced source capacity can no longer meet maximum day demand. In fact, our total system source capacity (<100 gpm from waterboy plus 0 gpm from well field) is only <43% of the required source capacity (based on maximum day demand our system must supply 250 gpm plus 20% safety factor). North Gualala Water Company community is in the state of a major water shortage and needs to supplement current sources immediately. | 10200000 | 1033 | 2595 | 03 | Mendocino | II | 2006
3301800-004 | 3301800 | STONEWOOD CANYON ESTATES | Stonewood Canyon Water Improvements | Stonewood Canyon Estates is seeking a low interest loan to fund the following improvements to their water system:1) Repair existing well liner and replacement existing failing pump. The well pump is rated for 15 gpm, but is pumping sand with a rate of 5 gpm.2) Replacement of damage storage tank roof.3)Replacement of 1200 feet of under sized pipelines from 1.5" sch. 40 pipes with 4" C900 PVC pipes.4) Replace old 1.5" non-operating gate valves with new 4" AWWA gate valves. | E | C | Stonewood Canyon Estate is experiencing the following problems:1) Low water pressure due to 1200 feet of undersized pipelines ( 1.5").2) Lost well production from 15 gpm to 5 gpm due to well pump damage and pumping sand.3) 67,000 gallon storage tank roof damage due to center support failure.4) Exiting water system can not be zoned of due to old non-opertion 1.5" valves. Total system has to be shut down for repairs. | 150000 | 26 | 40 | 20 | Riverside | V | 2013
2701422-001 | 2701422 | OAKRIDGE SUBDIVISION MWC | Source capacity project | Consolidation with Aromas Water District. | E | C | Insufficient source capacity - service connection moratorium in place. | 1000000 | 22 | 66 | 05 | Monterey | II | 1998
2310008-005 | 2310008 | Redwood Valley County Water District | Redwood Valley Off Stream Storage | Evaluate proposed off stream storage sites, including project design and environmental review. Also includes preliminary land survey. | E | C | Redwood Valley is currently under a court ordered moratorium that does not allow new services. The District is also subject to a Cease and Desist Order from DWR regarding annexed areas that are currently being served. This feasibility study would allow the District to explore the possibility of constructing off stream storage for high winter flows. Off stream storage would create a viable water supply that is currently lacking since the two primary water sales contracts that supply the District are both for surplus water subject to cut off during water short years. | 4000000 | 1339 | 3969 | 03 | Mendocino | II | 2007
2310008-008 | 2310008 | Redwood Valley County Water District | Redwood Valley Well Construction | The State Water Resources Control Board is urging this District to locate and develop a ground water source supplemental to its seasonal and surplus surface water supplies in order to avoid enforcement action. The District has identified three available agricultural properties that show promise for water supply wells. This project would fund up to three test wells, purchase of a property, two supply wells, and development of appropriate treatment to remove iron and manganese commonly found in the area. Additional costs would be power, security, and a pipeline to tie in to the existing distribution system. The estimated yield of 100-200 gpm would be sufficient to remove the threat of enforcement action and to provide emergency water supplies when the main source at Lake Mendocino is unavailable. | E | C | Redwood Valley CWD is under threat of enforcement action by the State Water Resources Control Board for providing water outside its place of use. The areas that are being served consist of four "annexations" on the edges of its recognized boundaries, including a small Rancheria with 30 homes. RVCWD has petitioned for a change of place of use, which is still pending. Such a change, if granted, would not remove the threat of enforcement action due to the seasonal and surplus nature of the other water supplies available to the district. RVCWD has been directed by the SWRCB to locate another source of water, preferably ground water, with which to serve these areas. | 3500000 | 1339 | 3969 | 03 | Mendocino | II | 2009
1510012-011 | 1510012 | Lamont Public Utility Dist | Lamont PUD Well #16 Water (Arsenic/Perchlorate) Treatment Project | The proposed project is for the purchase and installation of a 900 gpm BWIX/ Ion Exchange treatment and removal system for arsenic, and enhanced media for the removal of perchlorates. | F | C | Well #16 is producing water that exceeds the MCL for both Arsenic and Perchlorate. | 2000000 | 3603 | 13296 | 12 | Kern | III | 2009
5403110-001 | 5403110 | SIERRA MUTUAL WATER CO | Well Replacement and Nitrate Treatment | Water System is requesting funds to evaluate alternatives and to find the most cost effective solution to solving their water quality violation(s). The alternatives to be evaluated are as follows, and in no particular order: feasibility of consolidation with a nearby water system, centralized treatment, and replacement source(s). | F | C | Water System currently violates the Nitrate MCL. | 500000 | 15 | 39 | 12 | Tulare | III | 2012
2702094-002 | 2702094 | BLACKIE RD WS #18 | Blackie Road #18 | New water storage tank.backup power generator.Nitrate treatment plant. | F | C | Single well nitrate contamination, no emergency power.Tanks corroded, not acceptable designBankrupt systems | 800000 | 20 | 60 | 05 | Monterey | II | 2008
4000501-001 | 4000501 | HALCYON WATER SYSTEM | Ozone and filtering system | Central RO system or other treatment scheme to lower nitrate and selenium is needed. | F | C | water system exceeds the selenium and nitrate MCLs and is currently serving bottled water. | 100000 | 35 | 105 | 06 | San Luis Obispo | IV | 2011
2700665-001 | 2700665 | OAK HEIGHTS W & R CO INC | Funding for Compliance Order # 08-002, Nitrate Contaminant Removal | The following are suggested solutions to address the Nitrate Contaminant problem: (1) A certified professional install a reverse omosis system under the sink of every Oak Heights Water and Road Company, Inc., residence (35 units) (2) Install an Ion Exchange system at the well source. (3) Drill a new well and hope that the nitrate levels are in compliance. This would require additional pipe, connections and electrical hook ups. (4) Install a Nitrate Removal system and capture pond at the well source. This would require the expensive removal of nitrate sludge captured in the pond, which is considered a waste hazard (not cost effective. (5) Hire a certified blend operator, which requires constant monitoring (not cost effective). | F | C | The Oak Heighats Water and Road Company, Inc., has been notified by the Monterey County Department of Health that they are in violation of the California Safe Drinking Water Act and California Health and Safety Code Regulations (Section 64431 CCR/Section116555 HSC). A Compliance Order No. 08-002 was issued to the Oak Heights Water and Road Company, Inc., on March 25, 2008. The water systems nitrate levels exceded the legally permissible level of 45 mg/L. The Monterey County Department of Health ordered the Oak Heights Water and Road Company, Inc., to come into compliance by October 1, 2008. The water system is comprised mostly of fixed income families or families earning less than $45,000 per year. The water system does not have the monetary reserves/resources to finance a new water source (drilling a well), purchase equipment for treatment and monitoring the water system or hiring a certified blend operator. The Oak Heights Water and Road Company, Inc., cannot comply with the Monterey County Department of Healths compliance directive, without financial assistance. | 50000 | 35 | 105 | 05 | Monterey | II | 2008
2702007-002 | 2702007 | VIERRA ESTATES WS | Vierra Estates | New water storage tank (250,000 gallon).Emergency power generator.Nitrate treatment plant. | F | C | Single well nitrate contamination.Existing tank corroded, no useful life left.No back-up power.Many bordering residences desire to join system. | 900000 | 48 | 164 | 05 | Monterey | II | 2008
5400670-002 | 5400670 | TRIPLE R MUTUAL WATER CO. | Well Replacement and Nitrate Treatment | Water System is requesting funds to evaluate alternatives and to find the most cost effective solution to solving their water quality violation(s). The alternatives to be evaluated are as follows, and in no particular order: feasibility of consolidation with a nearby water system, POU/POE, centralized treatment, and replacement source(s). | F | C | Water System currently violates the Nitrate MCL. | 500000 | 130 | 400 | 12 | Tulare | III | 2012
5410007-003 | 5410007 | LSID - Tonyville | Tonyville Interconnection | A pipeline that interties the District and the City of Lindsay is needed to provide the District with water during canal water supply interruptions and eliminate the need to utilize nitrate-contaminated groundwater wells. The intertie also affords the opportunity for the District to pursue permanent domestic water system operations by the City of Lindsay. The proposed Project consists of the installation of an intertie pipeline between the Tonyville water distribution system and the City of Lindsay’s water system. This intertie will allow Tonyville to receive water from the City of Lindsay during periods when the Friant-Kern Canal is out of service and cannot deliver water for the Tonyville water treatment plant. The Project provides a dependable water supply during canal outages in the Friant-Kern Canal. In addition, this intertie will enable the District to eliminate its use of nitrate-contaminated wells. The proposed Project will consist of the design and construction of the interconnecting pipeline. The District and the City of Lindsay will also need to develop the terms and conditions for the operation and maintenance of the pipeline. The Department of Health Services is encouraging the District to consolidate its small domestic water systems into nearby domestic systems. The District will also pursue with the City of Lindsay a permanent consolidation of the Tonyville water system. The design component of the Project will consist of surveying, California Environmental Quality Act (CEQA) procedures, right-of-way acquisition and the detailed design of the improvements. The design of the pipeline will be straightforward. The Project is located in a rural area presenting few obstacles to the pipeline installation. The pipeline will be constructed in existing road rights-of-way and on private land. The Project will also require the acquisition of pipeline rights-of-way and issuance of roadway encroachment permits. The District proposes a 6-inch diameter pipeline. The pipeline will be approximately 14,000 feet in length. The design component of the Project will result in the preparation of the plans and specifications for bidding purposes. As part of the Project, the District will select a general contractor through a public bidding process. | F | C | The Lindsay-Strathmore Irrigation District (District) provides water for domestic and/or agricultural irrigation purposes. The District utilizes imported surface water as their primary water supply. The District has a contract for Class 1 water from the Central Valley Project. The water is delivered via the Friant-Kern Canal. The District owns and operates a water treatment plant that serves the Tonyville Tract. The Tonyville system serves approximately 50 connections. The District utilizes five (5) groundwater wells for the Tonyville system when surface water is not available. These wells, however, have nitrate levels that exceed the regulatory maximum concentration level (MCL). The nitrate concentrations ranged from 43 mg/l to 65 mg/l in twenty samples collected quarterly in 2006. The nitrate concentrations of the well water averaged approximately 54 mg/l. One well has not been utilized since 2005 due to high nitrate levels. The Friant-Kern Canal is dewatered every two to three years during the winter months for maintenance activities. In addition, the canal is subject to unscheduled outages that would disrupt the water supply. These situations result in the District having to utilize its nitrate-contaminated wells to meet domestic water demands. The District relies primarily on surface water for its domestic water supply for the Tonyville system. Since the District’s groundwater wells currently experience nitrate levels exceeding the MCL, interruptions to its surface water supply represent a serious concern. A new well drilled in this area is likely to have similar water quality and, therefore, not be useful for domestic consumption. The City of Lindsay’s water system has the capacity to deliver additional water to the significantly smaller Tonyville system. An intertie between the City of Lindsay and the Tonyville system would provide an alternate water supply to Tonyville eliminating the use of nitrate-contaminated groundwater wells. | 1038000 | 50 | 400 | 12 | Tulare | III | 2007
2701515-001 | 2701515 | MOSS LANDING HARBOR WS | Moss Landing | New well (minimum 350 gpm).Water treatment plant.Replacement of waterlines (12,000 ft.). | F | C | Single well nitrate contamination and seawater intrusion.Undersized asbestos cement waterlines. | 3500000 | 134 | 402 | 05 | Monterey | II | 2008
1910248-009 | 1910248 | LOS ANGELES CO WW DIST 37-ACTON | Application of Biological Denitrification for Nitrate Removal in Acton, CA | The purpose of this project is to implement a 1,000 gallons per minute (gpm) Biological Denitrification Water Treatment Plant for the District. The technology relies on utilizing naturally occurring bacteria in the groundwater to consume nitrate and convert it to nitrogen gas, N2. The treatment system includes four treatment processes: A biological contactor in which nitrate is removed, an aeration contactor in which oxygen is added to the water and excess nitrogen gas is removed from the water, a filtration process to remove particles and bacteria present in the effluent of the biological contactor, and a disinfection process aimed at meeting the minimum disinfection requirements set by the California Department of Public Health (CDPH) for groundwater BDN treatment systems. Acetic acid (vinegar) is added to the water as it enters the treatment plant. The acetic acid is the food source used by the natural bacteria to consume nitrate. A low dose of phosphorus is added as a nutrient to promote efficient bacterial growth. Other chemicals added at the plant include a coagulant to help filter performance, and chlorine to meet the disinfection requirements. The District partnered with the Water Research Foundation to co-fund a 2 gpm pilot-scale study by Water Quality Treatment Solutions Inc. aimed at evaluating nitrate removal from District 37 groundwater. The study is ongoing, but sufficient data and information have been gathered to provide the District with an understanding of the configuration and cost of a 1000-gpm BDN treatment system. The average nitrate level in the groundwater was measured at approximately 8.5 mg/L as N. Within five days of startup, nitrate was reduced to less than 4 mg/L as N, and after 10 days of operation, the nitrate reached its target treated-water level of 1 to 2 mg/L as N. Pilot testing results to-date show that the waste backwash water can be clarified and returned to the head of the treatment plant. With clarification and recovery, the wastage rate from the pilot plant was reduced from 8% without wastewater recovery to approximately 0.33% with wastewater recovery. | F | C | Elevated nitrate levels in groundwater supplies are a significant problem across California and the nation. In most situations, elevated nitrate levels are caused by excess fertilizer applications in agricultural areas. However, it could also be caused by leaching from underground septic systems. Due to its adverse health effects, nitrate is strictly regulated in drinking water, with a drinking water maximum contaminant limit (MCL) of 45 mg/L; also expressed as 10 mg/L as N. The adverse health effects of nitrate are acute. The health concern over the presence of nitrate in water is related to its reduction to nitrite in the digestive system. When absorbed into the bloodstream, nitrite hinders the blood’s ability to transport oxygen to the cells. Infants are most susceptible to nitrite poisoning because their digestive systems contain high levels of bacteria that convert nitrate to nitrite. For this reason, exceedance of the nitrate MCL requires a water system to issue a public notification within 24-hrs of becoming aware of such exceedance.The Los Angeles County Waterworks District 37 (District) owns and operates three wells in Acton, California, which contain elevated levels of nitrate ranging from 3.7 mg/L as N to 10.0 mg/L as N. The District currently relies on blending of the three wells as the sole strategy to maintain nitrate below its regulatory limit. However, blending is not a long-term solution as Nitrate levels are increasing with demand.Conventional nitrate removal technologies include ion-exchange and reverse osmosis. Both technologies are proven drinking water treatment technologies. Unfortunately, they both generate a high-salinity waste stream that has very limited disposal options. For the District, there is no viable local disposal option for such a waste stream, which renders both technologies inapplicable for nitrate removal from District 37 wells. | 8500000 | 1377 | 4282 | 16 | Los Angeles | IV | 2013
5410010-012 | 5410010 | Porterville, City of | New water source and interconnect 7 adj sws w nitrate contam | The City needs to construct three new wells and construct hookups to each system with a master meter and a backflow prevention device. | F | C | The City's water system is needed to supply water to seven different privately owned public water systems located around the periphery of the City limits. These systems have nitrates that exceed the MCL. | 2100000 | 14562 | 51467 | 12 | Tulare | III | 2004
5410010-014 | 5410010 | Porterville, City of | Consolidation of Private water Companies | The three private water companies located along the edge of City limits repeatly ask that the City of Porterville provide water to their private water delivery system via a master meter.City policy requires that private water companies abandon their offending wells, pay all connection fees and annex to the City. if funding thorugh this program becomes available, staff will propose to the City Council that annexation not be mandatory. Funding will pay for the design of a new water delivery systems, anticipated to range in pipe size from 4 to 8" in diamter, abandonment of the existing private wells, installation of indivdual meters and connection to the city's main water grid. | F | C | The City is surrounded by private water companies whose wells exceed the MCL level for nitrates. If funded, staff will recommend to the City Council that plans & specification be drawn to abandon the offending private wells and piping system. The City will construct a new water delivery system (new pipelines), install new meters at each residence and connect the new system to the City's water system. | 2000000 | 14562 | 51467 | 12 | Tulare | III | 2009
1000160-001 | 1000160 | FRESNO RIFLE & PISTOL CLUB | Nitrate MCL Exceedance - Alternative Evaluation | The Water System continues to monitor quarterly for nitrate in the raw water and seeks to identify potential solutions to resolve this issue. Unless the water quality dramatically and reliably improves, the Water System plans to investigate: treatment, point-of-use treatment, source improvements or replacement. | F | N | The Water System's single source of water produces levels of nitrate that have exceeded the nitrate MCL (45mg/L) in the past. The Water System had operated under a handwashing exemption, until repeal by legislative action. Since 2008, nitrate monitoring has ranged between 14 mg/L and 58 mg/L, with an average of 39 mg/L. The well does not reliably produce water with nitrate levels below the nitrate MCL. | 500000 | 1 | 30 | 23 | Fresno | III | 2013
5101009-002 | 5101009 | Wildwood East Mutual | Consolidation of Wildwood East water system with Franklin School District | I am assuming that all of the above is covered by the overall grant . The project will include each addition to the Franklin grant. All of the additions including Wildwood East are located north off Franklin blvd. The plan is to run a water line from the main feeder water line on Franklin down each street in each area to which the individual homes will be connected. The connection to each home will be part of the grant. The connection from the well that currently provides water will be disconnected. However, the well water will continue to be used for landscaping by hooking into the outside water lines already established. | G | C | The Wildwood Water District would like to be included in the Franklin School District grant along with the three other small private water systems already included in the grant. We have been informed that our water purity is no longer in compliance with the EPA standards for the amount of arsinec allowed in the water which is 10pbb. We have been notified that our present test results for arsinec is 13ppb. We understand that future tests are requried to average 10.4 or above.This score is no surprise as we have been aware of the gradual increas in the arsinec contamination over the past years.When tested for arsenic the Wildwood East Water district has tested:5ppb in year 2000, 5 ppb in 2001, 12 ppb in 2002, 8.8 ppb in 2005 and 2006. 9.7 ppb in 2008 and 2009, 10.0 ppb in 2010 and 13 ppb in2011 which puts our District out of compliance like the other water districts ( trailer park, El Margarita Water District, and Wildewood Water District). Now all of those areas exceed the State standard for contaminent and, because of this, fall under a grant for the Franklin Elementary School District. Given that our District is no longer in compliance, Wildwood East Water District would like to be included in the grant for the Franklin Elementary School District. We are geographicly located in the middle of the other applicants, our kids attend Franklin Elementary. Moreover, since the group that is most likely to be affected the most by arsenic are children, especially pre school and children in Elementary school, We are concerned as we have several new babies in the area and many students who attend Franklin Elementary. | 1000000 | 49 | 350 | 21 | Sutter | I | 2012
2000501-001 | 2000501 | BASS LAKE ANNEX #3 | Removal of Uranium/Gross Alpha | The water company is currently investigating the procedures and equipment to complete treatment required and determine the cost thereof. | G | C | Elimination of uranium and gross alpha from water per Title 22, California Code of Regulations, Section 64442 | 75000 | 23 | 42 | 11 | Madera | III | 2007
1500461-001 | 1500461 | FOUNTAIN TRAILER PARK WATER | Arsenic compliance | Connection to North Edwards Water District (System no. 1510052) | G | C | Arsenic above MCL | 187000 | 32 | 68 | 19 | Kern | III | 1999
2701670-002 | 2701670 | LANGLEY/VALLE PACIFICO WS | Langley/Valle Pacifico Well Replacement/Pipeline Project | The proposed project will include the drilling and development of an offsite well and a delivery pipeline to provide an alternative source of water for the Langley/Valle Pacifico system. The project will include additional storage tanks and not more than two pump stations. | G | C | The wells that provide water to the Langley/Valle Pacifico system all contain arsenic. The largest and primary well has arsenic levels that exceed "action levels". These levels constitute a clear threat to the health and safety of the residents of the area. Additionally, due to the proliferation of septic tanks in the area, nitrate levels in groundwater are beginning to rise. These contaminate levels have been recognized and identified by both the Monterey County Department of Environmental Health and the California Department of Public Health. | 480000 | 27 | 81 | 05 | Monterey | II | 2007
2000524-002 | 2000524 | SKY ACRES MUTUAL WATER CORP | Well Replacement and Arsenic Treatment | Water System is requesting funds to evaluate alternatives and to find the most cost effective solution to solving their water quality violation(s). The alternatives to be evaluated are as follows, and in no particular order: feasibility of consolidation with a nearby water system, POU/POE, centralized treatment, and replacement source(s). | G | C | Water System currently violates the Arsenic MCL. | 500000 | 50 | 90 | 11 | Madera | III | 2012
2000524-001 | 2000524 | SKY ACRES MUTUAL WATER CORP | Research replacement water well | Planning to drill a replacement well. Feasibility studies with the Board of Directors will be considered. Consolidation is not an option as there are no other water Co .nearby. Possibility of another storage tank which would include purchasing land from National Forest Service. | G | C | Deep water well #3 exceeds the drinking water MCL standards because of arsenic contamination. This well was in violation of arsenic level standards. Al customers were notified via General Meeting & postings throughout subdivision. Temporary solution has been to blend all water sources together until County of Madera comes up with solid plan to address tghis problem. | 100000 | 50 | 90 | 11 | Madera | III | 2012
1000238-001 | 1000238 | CAMDEN TRAILER PARK | New well to augment single well | Drill a new well or interconnect if possible. | G | C | System supplied by one well. If it goes out due to drought the system will be out of water. | 200000 | 25 | 90 | 23 | Fresno | III | 2008
3400169-003 | 3400169 | SPINDRIFT MARINA | water treatment funding | Seeking professional reccomendations on re-working or re-building our water treatement plant, so as to comply with removal of chemical contamination. | G | C | Arsenic water sampling exceeds the MCL. Current count is between 20 - 23. Iron and Manganese counts exceed the MCL. Received county notice of Arsenic, Iron, & Manganese MCL Violations. | 25000 | 25 | 100 | 09 | Sacramento | I | 2012
3700041-002 | 3700041 | BARRETT LAKE MH AND RV LLC | Treatment of water source for removal of radionuclides | Propose to install radionuclide treatment on the well with the highest level of radionuclides and highest water well yield. Once treated, the source water wells will be blended to bring the system water below the EPA MCL. Proposed treatment is an inline filtration system consisting of a "filter resin" to reduce the levels of radionuclide contaminants below the MCL. Currently the two wells are connected to pump directly to the storage tanks and no water service connections lie between the wells and storage tanks. Project will incude the treatment filter vessel with media/piping, housing structure and slab, plumbing and related electrical controls and well head upgrade. | G | C | Both water wells exceed the EPA MCL for Gross Alpha and Uranium of 15 pCi/l and 20 pCi/l, respectively. A Tier 2 Public Notification was issued on March 25, 2009 and remains in effect. | 80000 | 94 | 160 | 14 | San Diego | V | 2009
5100107-007 | 5100107 | Sutter Co. WWD#1 (Robbins) | Construction of a New Robbins Water Treatment Plant and Arsenic Removal System | In order to achieve compliance with primary and secondary MCLs, the existing water treatment plant must be moved to the larger Sacramento Valley Boulevard site to accommodate new water treatment equipment. Water is distributed through a system of mains ranging from 3” to 12” in diameter. The current system is comprised of approximately 4 miles of water piping and valves, and 94 lateral connections. A new public water well will be drilled and developed at a new site. Currently, the County is leasing 0.06 acres from Wagner Aviation for the existing well site. The new well site is located on Sacramento Valley Boulevard. The land is owned by the County and is approximately 0.67 acres.Major equipment at the new water plant will include: a new drilled well, arsenic filtration system, iron and manganese removal equipment, a backwash tank, a water storage tank, well pump equipment, booster pump station, electrical supply equipment, chemical feed system and a hydro pneumatic tank. However, before construction of the new water treatment plant can begin, the existing water tower located at the Sacramento Valley site will be demolished. | G | C | The Sutter County – Water Works District No. 1 (WWD#1) is responsible for providing water service to the Community of Robbins. The water system currently operates one active ground water well (Wagner Well), one backup ground water well and one storage tank that provides the Community’s residents with potable water. The active ground water well incorporates treatment for iron and manganese. The system provides municipal drinking water to approximately 336 year-round residents. The total system was designed to meet all health standards when constructed; however, due to a recent change in the Federal arsenic limit, the system does not meet the new primary Maximum Contaminate Level (MCL) for arsenic. The Wagner Well also exceeds secondary MCLs for chloride, specific conductance, and manganese. Currently, the one active ground water well is located on land leased to WWD#1 by Wagner Aviation. The “Maximum Contaminant Level” (MCL) for arsenic in drinking water was recently lowered from 50 parts per billion (ppb) to 10 ppb. The existing filter media at the water treatment plant was not designed to reach this level of arsenic removal, and is not meeting either State or Federal requirements for the removal of arsenic. Similarly, the existing filter media is not meeting secondary standards for manganese, chloride, and specific conductance for treated water. On January 2, 2009, the California Department of Public Health issued Compliance Order No. 01-21-09(O) 51001 for non-compliance with the new MCL for arsenic of 10ug/l (micro-grams per liter) for the Community of Robbins. The revised arsenic standard was adopted by the State of California on November 28, 2008. The average arsenic concentration of the treated water at the Wagner Well, based upon four consecutive quarterly samples completed during calendar year 2008, was 18.1ug/l. Currently there is a building moratorium in the Community of Robbins due to a lack of capacity at the water treatment plant and wastewater treatment plant. Any new development within the Community of Robbins would require significant capital improvements to the water and wastewater systems. In addition to constructing a new water treatment plant, new distribution piping would be required before new development could occur. WWD#1 is not considering expansion of the water or wastewater plant at this time. | 2409000 | 94 | 336 | 21 | Sutter | I | 2011
5101009-001 | 5101009 | Wildwood East Mutual | Water System Consolidation | Copnsolidate community drinking water system with near by City of Yuba City public water system to meet drinking water quality regulatory compliance. | G | C | High Priority - Water system is on the brink of exceeding allowable arsenic limits in drinking water. Nitrate levels in existing wells are increasing and could cause system to be out of GW regulatory compliance. | 1550000 | 49 | 350 | 21 | Sutter | I | 2009
2410011-005 | 2410011 | LE GRAND COMM SERVICES DIST | Le Grand Community Services District Arsenic treatment | Le Grand Community Services DistrictArsenic TreatementThe proposed project would be to install aresnic removal and treatment equipment at the two well sites. | G | C | Le Grand Community Services DistrictAresenic treatmentThe district has three operational wells that serve the community for the required water distribution to the customers. All of these wells have a low yield as the aquifer in the area does not provide for large water removal. Two of the three wells have an arsenic level that exceeds the allowable 10 ppb MCL. | 1750000 | 501 | 1700 | 11 | Merced | III | 2009
3210011-004 | 3210011 | Plumas Eureka CSD | Plumas Eureka CSD - Water System Improvement Project | New water well and arsenic treatment facility, installation of hypochlorite generators in place of existing chlorine gas units. | G | C | Plumas Eureka CSD is in violation of the Arsenic MCL drinking water standard. | 5000000 | 547 | 1785 | 02 | Plumas | I | 2012
5510008-011 | 5510008 | LAKE DON PEDRO C S D | Clarification Basin Building Completion | Pour a concrete foundation with drainage system for the metal building that will be placed over the clarification basin. Construct the metal building that has already been purchased. Most of the engineering work has been completed for this project. With the required funding in place, this project can be started immediately. | G | C | The district is currently out of compliance with our Trihalomethanes (THM). They are above the Drinking Water Standard. We should be at 80 micrograms per liter. Last quarter we reported a level of 83.6. The standard is set to be lowered in the future so we will be even further out of compliance. By covering our open clarification basin, it will reduce the entry and growth of organic material and increase the effectiveness of our polymers, reducing our THM levels. The metal building has been purchased and is on site, but funds are not available to complete the project. Our district is facing our fourth year of constrained revenues due to the economic downturn in our isolated, rural community which has resulted in three years of unbalanced budgets. The Department of Public Health is requiring us to complete this project as a part of upgrading our facilities in order to meet the water quality standards they desire. | 140000 | 1442 | 3600 | 11 | Tuolumne | III | 2009
1510018-005 | 1510018 | ROSAMOND CSD | Arsenic treatment for Well 7 | Install package arsenic removal plant at one well that will be used to remove arsenic from water of two wells (Wells 8 and 9). Blend this water with other well water to get arsenic level below 10 ug/L. | G | C | Rosamond CSD has four wells and all of them are 10 ug/l or higher for arsenic, thereby exceeding the new federal arsenic MCL of 10 ug/L.. Well #7 water exceeds MCL for arsenic. | 250000 | 4593 | 10633 | 19 | Kern | III | 2006
1510018-004 | 1510018 | ROSAMOND CSD | Arsenic treatment for Wells 8 & 9 | Install package arsenic removal plant at one well that will be used to remove arsenic from water of two wells (Wells 8 and 9). Blend this water with other well water to get arsenic level below 10 ug/L. | G | C | Rosamond CSD has four wells and all of them are 10 ug/l or higher for arsenic, thereby exceeding the new federal arsenic MCL of 10 ug/L | 950000 | 4593 | 10633 | 19 | Kern | III | 2005
1910070-039 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Improving Water Quality in the Ana Verde Tanks | The purpose of the proposed project is to thoroughly mix the water in the tank to eliminate temperature stratification and stagnant water conditions, which will provide a uniform, short water age. To accomplish this goal, the District proposes using one of the commercially available tank mixing devices. The mixing device has little to no energy cost and requires virtually no maintenance, since it is powered by a solar panel placed on the top of the tank. This system efficiently mixes all the water in the tanks by creating a near-laminar flow pattern, which will reach and eliminate all the dead spots. The device will also be equipped with Supervisory Control and Data Acquisition (SCADA) output signals that allow for real-time monitoring of the tank; and a chlorine injection system that will help maintain appropriate disinfectant levels in the tanks.This mixing device, which consists of three floats in triangular pattern with total float buoyancy of 600 pounds, floats on the water surface with a down intake hose to draw water. The variable length hose automatically adjusts for peak performance at any water depth. The intake remains stationary just above and in contact with bottom of the tank, preventing the mixer from moving out of place or rotating. This device is capable of pumping about 10,000 gallons per minute for mixing. By using this mixing device, fewer chemicals will be needed when boosting and TTHM formation will be reduced. In addition, this mixing device reduces residual chlorine loss and nitrification, reduces water treatment costs, ensures compliance with the Disinfection Byproduct Rule and/or Total Coliform Rule, and enables the District to provide high quality water for its customers.Through the Proposition 50 grant funding from the State, a solarbee tank mixer was recently installed in the 0.5 million gallon Cuyama Tank within the District’s Lake Los Angeles water system. Before installation of the mixer on July 24, 2008, the water temperature in the tank varied by 8.1 degrees Fahrenheit from the surface to six meters in depth. The temperature difference was reduced to 3.7 degrees Fahrenheit after only one day of tank mixing, proving that the mixer effectively eliminated thermal stratification and provided uniform, short water age.The estimated total capital cost of the mixing device is $80,000. | G | C | The Los Angeles County Waterworks District No. 40 receives its water supply from the Antelope Valley-East Kern Water Agency (AVEK) and the District’s wells in the Antelope Valley Groundwater Basin. AVEK gets its water from the Sacramento River/San Joaquin Delta via the State Water Project. The water supplied by AVEK is currently disinfected with chlorine and AVEK plans to switch disinfection to chloramines in 2009 Within the District, the Ana Verde tanks located at 2700 Moonwort Court have a total capacity of 4,260,000 gallons; 2 tanks with 2,130,000 gallons. Long storage times and the lack of mixing of water in the storage facilities often promote formation of disinfection byproducts that may cause liver, kidney, or central nervous system problems and may increase the risk of cancer. Once chloramination begins in 2009, the situation is likely to foster nitrification that occurs when the chloraminated water has excess ammonia present in the distribution system. Nitrification can have adverse effects on water quality, including a loss of total chlorine, an increase in heterotrophic plate count bacteria concentration, and potential increases in total coliforms. A violation of the USEPA Disinfection Byproduct Rule (DBPR) and/or Total Coliform Rule may lead to severe customer illness throughout the District.Air temperature in the District is consistently high during the summer months, averaging 89, 95, 95, and 88 degrees Fahrenheit in June, July, August and September, respectively. Higher air temperatures significantly increase the temperature of water already in the tanks. The groundwater, which enters the bottom of the tank is much cooler, resulting in the hot, less dense water stagnating at the top. The stagnant hot water in the tank tends to have long residence times, promoting growth of bacteria and formation of disinfection by-products.The District does not collect disinfection byproduct samples within the tanks; however, samples in the distribution system were taken under the Stage 1 DBPR. Between February 2004 and July 2008, the District collected 564 Total Trihalomethanes (TTHM) samples, which is one of the disinfection byproducts required to be monitored under the Stage 1 DBPR. These samples were gathered from the District’s Lancaster and Desert View Highlands water system. The TTHM levels ranged from 0.0 parts per billion (ppb) to 166.0 ppb and were above the Maximum Contaminant Level of 80 parts ppb 103 times during this period. In addition, the water provided by AVEK has continuously been increasing in TTHM levels. For example, in July 2008, AVEK provided the District with water containing 119 ppb of TTHMs. | 40000 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910070-031 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Arsenic Treatment in Well 4-83 | This project will reduce arsenic levels from the groundwater pumped from Well No. 4-83 ensuring compliance with the new arsenic standard of 10 ppb. To accomplish this goal, the District proposes using one of the commercially available ion exchange systems for arsenic treatment. Ion exchange is designated as the Best Available Technology by the US EPA for the removal of arsenic from drinking water sources. Several ion exchange treatment systems have already been permitted by the California Department of Public Health and are in operation in the State. A typical ion exchange treatment system is simple, robust, compact, easy to automate, and can be operated on demand. The treatment goal is to reduce the arsenic in the effluent (treated) water to less than 4 ppb. The proposed packaged wellhead arsenic removal system includes a treatment module, pre-filter assembly, salt/saturator tank, brine processing unit, and brine wastewater storage tank(s). Details of each component that is sized to treat the flow rate from Well No. 4-83 at 1,000 GPM are as follows. The treatment module (i.e., ion exchange system) uses multiple columns of ion exchange resin operating in parallel to remove the arsenic from the well water. The columns are installed in a 10’W x35’L x 9’H mobile container, eliminating the need for a building or other housing structures. The ion exchange resin is regenerated using a sodium chloride (salt) solution. The treatment module is equipped with a pre-filter assembly consisting of canisters with easy removable lids that allow for the quick replacement of filter elements. The filter assembly’s purpose is to collect large particulate matter before it enters the ion exchange beds keeping them from fouling up and eliminating the need for backwash. A salt storage container (6,800 gallons) is installed to function as the saturator where the concentrated salt/water solution is produced for the onsite regeneration of the ion exchange resin. A brine processing unit (10’W x 20’L x 9’H) is designed for processing the brine wastewater produced from the onsite regeneration of the ion exchange resin. This process employs a precipitation step that binds the arsenic and renders the brine non-hazardous. It also employs a filtration process that separates the solids from the liquid. Two 3,000 gallon tanks for the storage of the spent brine wastewater are installed. The estimated total cost of the above treatment system is $702,260. | G | C | This project targets arsenic contamination in drinking water. Arsenic has been shown to negatively impact human health and is considered one of the primary causes of cancer in the world. The Safe Drinking Water Act Amendment of 1996 required the United States Environmental Protection Agency (USEPA) to establish a new drinking water standard for arsenic. In January 2001, the USEPA adopted a new arsenic standard of 10 parts per billion (ppb). The new standard became effective in January 2006.The Los Angeles County Waterworks District No. 40, Antelope Valley, Regions 4 & 34, Lancaster and Desert View Highlands (Regions), serves approximately 145,000 people through over 47,000 service connections in the Lancaster and Palmdale areas of the Antelope Valley. During 2007, groundwater made up approximately 39 percent of the water supply in the Regions. The groundwater is extracted from 33 wells drilled into the aquifers in the Lancaster Subunit of the Antelope Valley Groundwater Basin which is impacted by arsenic found naturally in rocks and minerals. In order to increase water supply reliability, the District recently drilled Well No. 4-83 at 419 West Avenue J, Lancaster. This well is projected to provide water at the rate of 1,000 gallons per minute (GPM). However, analysis of a water sample collected on December 12, 2007 showed an arsenic concentration of 9.53 ppb, just below the new standard by 0.47 ppb. Therefore, the District proposes the following project for Well No. 4-83 to ensure long-term compliance with the arsenic standard and a high quality of water supply for our customers. | 632034 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910070-035 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Improving Water Quality in the Tierra Subida Tanks | The purpose of the proposed project is to thoroughly mix the water in the tank to eliminate temperature stratification and stagnant water conditions, which will provide a uniform short water age. To accomplish this goal, the District proposes using one of the commercially available tank mixing devices. The mixing device has little to no energy cost and requires virtually no maintenance, since it is powered by a solar panel placed on the top of the tank. This system efficiently mixes all the water in the tanks by creating a near-laminar flow pattern, which will reach and eliminate all the dead spots. The device will also be equipped with Supervisory Control and Data Acquisition (SCADA) output signals that allow for real-time monitoring of the tank and a chlorine injection system that will help maintain appropriate disinfectant levels in the tank.This mixing device, which consists of three floats in triangular pattern with total float buoyancy of 600 pounds, floats on the water surface with a down intake hose to draw water. The variable length hose automatically adjusts for peak performance at any water depth. The intake remains stationary just above and in contact with the bottom of the tank, preventing the mixer from moving out of place or rotating. This device is capable of pumping about 10,000 gallons per minute for mixing. By using this mixing device, fewer chemicals will be needed when boosting and TTHM formation will be reduced. In addition, this mixing device reduces residual chlorine loss and nitrification, reduces water treatment costs, ensures compliance with the Disinfection Byproduct Rule and/or Total Coliform Rule, and enables the District to provide high quality water for its customers.Through the Proposition 50 grant funding from the State, a solarbee tank mixer was recently installed in the 0.5 million gallon Cuyama Tank within the District’s Lake Los Angeles water system. Before installation of the mixer on July 24, 2008, the water temperature in the tank varied by 8.1 degrees Fahrenheit from the surface to six meters in depth. The temperature difference was reduced to 3.7 degrees Fahrenheit after only one day of tank mixing, proving that the mixer effectively eliminated thermal stratification and provided uniform, short water age.The estimated total capital cost of the mixing device is $80,000. | G | C | Los Angeles County Waterworks District No. 40 receives its water from the Antelope Valley-East Kern Water Agency (AVEK) and the District’s wells in the Antelope Valley. AVEK currently disinfects with chlorine but plans to switch to chloramines in 2009. Within the District, the two Tierra Subida Tanks located at 38301 N. Tierra Subida West have a total storage capacity of 4,800,000; 2,800,000 and 2,000,000 gallons. The tanks have a common inlet/outlet connection. This connection is sized for throughput capacity at minimum head loss, resulting in a very low flow velocity into the tank during filling. This low velocity results in poor mixing within the tanks, leading to stagnation. In addition, the freshest water added to the tank is the first to be drawn out. This process leads to thermal stratification within the tank since fresh cold water stays near the base and warmer, older water stagnates near the top. Long storage times and lack of mixing water in the storage facilities promotes formation of disinfection byproducts that may cause liver, kidney, or central nervous system problems and may increase the risk of cancer. Once chloramination begins in 2009, the situation is likely to foster nitrification that occurs when the chloraminated water has excess ammonia present in the distribution system. Nitrification can have adverse effects on water quality, including a loss of total chlorine, an increase in heterotrophic plate count bacteria concentration, and potential increases in total coliforms. A violation of the USEPA Disinfection Byproduct Rule (DBPR) and/or Total Coliform Rule may lead to severe customer illness throughout the District. Air temperature in the District is consistently high during summer months averaging 89, 95, 95, and 88 degrees Fahrenheit in June, July, August and September, respectively. Higher temperatures significantly increase the temperature of water already in the tanks. The groundwater, which enters the bottom of the tank, is much cooler, resulting in the hot, less dense water stagnating at the top. Temperature measurements were taken at different depths within the tanks during August 2008. The temperature readings were 82.7 and 80.4 degrees Fahrenheit at the top and bottom, respectively. The 2.3 degree difference in temperature at different depths indicates uneven mixing, increasing the potential for stagnant areas to form, promoting the formation of disinfection by-products. Disinfection byproduct samples are not collected within the tanks; however, samples in the distribution system were taken under the Stage 1 DBPR. Between February 2004 and July 2008, the District collected 564 Total Trihalomethanes (TTHM) samples, which is one of the disinfection byproducts required to be monitored under the Stage 1 DBPR. These samples were gathered from the District’s Lancaster and Desert View Highlands water system. The TTHM levels ranged from 0.0 parts per billion (ppb) to 166.0 ppb and were above the Maximum Contaminant Level of 80 ppb 103 times during this period. The water provided by AVEK has continuously been increasing in TTHM levels. For example, in July 2008, AVEK provided the District with water containing 119 ppb of TTHMs. | 40000 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910070-040 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Improving Water Quality in the Rancho Vista Tanks | The purpose of the proposed project is to thoroughly mix the water in the tank to eliminate temperature stratification and stagnant water conditions, which will provide a uniform short water age. To accomplish this goal, the District proposes using one of the commercially available tank mixing devices. The mixing device has little to no energy cost and requires virtually no maintenance, since it is powered by a solar panel placed on the top of the tank. This system efficiently mixes all the water in the tanks by creating a near-laminar flow pattern, which will reach and eliminate all the dead spots. The device will also be equipped with Supervisory Control and Data Acquisition (SCADA) output signals that allow for real-time monitoring of the tank and a chlorine injection system that will help maintain appropriate disinfectant levels in the tank.This mixing device, which consists of three floats in triangular pattern with total float buoyancy of 600 pounds, floats on the water surface with a down intake hose to draw water. The variable length hose automatically adjusts for peak performance at any water depth. The intake remains stationary just above and in contact with the bottom of the tank, preventing the mixer from moving out of place or rotating. This device is capable of pumping about 10,000 gallons per minute for mixing. By using this mixing device, fewer chemicals will be needed when boosting and TTHM formation will be reduced. In addition, this mixing device reduces residual chlorine loss and nitrification, reduces water treatment costs, ensures compliance with the Disinfection Byproduct Rule and/or Total Coliform Rule, and enables the District to provide high quality water for its customers.Through the Proposition 50 grant funding from the State, a solarbee tank mixer was recently installed in the 0.5 million gallon Cuyama Tank within the District’s Lake Los Angeles water system. Before installation of the mixer on July 24, 2008, the water temperature in the tank varied by 8.1 degrees Fahrenheit from the surface to six meters in depth. The temperature difference was reduced to 3.7 degrees Fahrenheit after only one day of tank mixing, proving that the mixer effectively eliminated thermal stratification and provided uniform, short water age.The estimated total capital cost of the mixing device is $80,000. | G | C | The Los Angeles County Waterworks District No. 40 receives its water from the Antelope Valley-East Kern Water Agency (AVEK) and the District’s wells in the Antelope Valley. AVEK currently disinfects with chlorine but plans to switch to chloramines in 2009. Within the District, the two Rancho Vista tanks located at 40400 Gemelos Court each have a storage capacity of 3,800,000 gallons. The tanks have a common inlet/outlet connection. This connection is sized for throughput capacity at minimum head loss, which results in a very low flow velocity into the tank during filling. This low velocity results in poor mixing within the tanks, leading to stagnation. In addition, the freshest water added to the tank is the first to be drawn out. This process leads to thermal stratification within the tanks since fresh cold water stays near the base and warmer, older water stagnates near the top. Long storage times and the lack of mixing of water in the tank promotes formation of disinfection byproducts that may cause liver, kidney, or central nervous system problems and may increase the risk of cancer. Once chloramination begins in 2009, the situation is likely to foster nitrification that occurs when the chloraminated water has excess ammonia present in the distribution system. Nitrification can have adverse effects on water quality, including a loss of total chlorine, an increase in heterotrophic plate count bacteria concentration, and potential increases in total coliforms. A violation of the USEPA Disinfection Byproduct Rule (DBPR) and/or Total Coliform Rule may lead to severe customer illness throughout the District. Air temperature in the District is consistently high during summer months averaging 89, 95, 95, and 88 degrees Fahrenheit in June, July, August and September, respectively. Higher temperatures significantly increase the temperature of water already in the tanks. The groundwater, which enters the bottom of the tank, is much cooler, resulting in the hot, less dense water stagnating at the top. Temperature measurements were taken at different depths within the tanks during August 2008. The temperature readings were 79.1 and 83.7 degrees Fahrenheit at the top and bottom, respectively. The 4.6 degree difference in temperature at different depths indicates uneven mixing, increasing the potential for stagnant areas to form, promoting the formation of disinfection by-products.Disinfection byproduct samples are not collected within the tanks; however, samples in the distribution system were taken under the Stage 1 DBPR. Between February 2004 and July 2008, the District collected 564 Total Trihalomethanes (TTHM) samples, which is one of the disinfection byproducts required to be monitored under the Stage 1 DBPR. These samples were gathered from the District’s Lancaster and Desert View Highlands water system. The TTHM levels ranged from 0.0 parts per billion (ppb) to 166.0 ppb and were above the Maximum Contaminant Level of 80 ppb 103 times during this period. In addition, the water provided by AVEK has continuously been increasing in TTHM levels. For example, in July 2008, AVEK provided the District with water containing 119 ppb of TTHMs. | 40000 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910070-030 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Improving Water Quality in the M-5E Tanks | The purpose of the proposed project is to thoroughly mix the water in the tank to eliminate temperature stratification and stagnant water conditions, which will provide a uniform short water age. To accomplish this goal, the District proposes using one of the commercially available tank mixing devices. The mixing device has little to no energy cost and requires virtually no maintenance, since it is powered by a solar panel placed on the top of the tank. This system efficiently mixes all the water in the tanks by creating a near-laminar flow pattern, which will reach and eliminate all the dead spots. The device will also be equipped with Supervisory Control and Data Acquisition (SCADA) output signals that allow for real-time monitoring of the tank and a chlorine injection system that will help maintain appropriate disinfectant levels in the tank.This mixing device, which consists of three floats in triangular pattern with total float buoyancy of 600 pounds, floats on the water surface with a down intake hose to draw water. The variable length hose automatically adjusts for peak performance at any water depth. The intake remains stationary just above and in contact with the bottom of the tank, preventing the mixer from moving out of place or rotating. This device is capable of pumping about 10,000 gallons per minute for mixing. By using this mixing device, fewer chemicals will be needed when boosting and TTHM formation will be reduced. In addition, this mixing device reduces residual chlorine loss and nitrification, reduces water treatment costs, ensures compliance with the Disinfection Byproduct Rule and/or Total Coliform Rule, and enables the District to provide high quality water for its customers.Through the Proposition 50 grant funding from the State, a solarbee tank mixer was recently installed in the 0.5 million gallon Cuyama Tank within the District’s Lake Los Angeles water system. Before installation of the mixer on July 24, 2008, the water temperature in the tank varied by 8.1 degrees Fahrenheit from the surface to six meters in depth. The temperature difference was reduced to 3.7 degrees Fahrenheit after only one day of tank mixing, proving that the mixer effectively eliminated thermal stratification and provided uniform, short water age.The estimated total capital cost of the mixing device is $80,000. | G | C | The Los Angeles County Waterworks District No. 40 receives its water from the Antelope Valley-East Kern Water Agency (AVEK) and the District’s wells in the Antelope Valley. AVEK currently disinfects with chlorine but plans to switch to chloramines in 2009. Within the District, the three M-5E tanks located at 41956 5th Street East each have a storage capacity of 3,000,000 gallons. The tanks have a common inlet/outlet connection. This connection is sized for throughput capacity at minimum head loss, resulting in a very low flow velocity into the tank during filling. This low velocity results in poor mixing within the tanks, leading to stagnation. In addition, the freshest water added to the tank is the first to be drawn out. This process leads to thermal stratification within the tank since fresh cold water stays near the base and warmer, older water stagnates near the top. Long storage times and lack of mixing water in the storage facilities promotes formation of disinfection byproducts that may cause liver, kidney, or central nervous system problems and may increase the risk of cancer. Once chloramination begins in 2009, the situation is likely to foster nitrification that occurs when the chloraminated water has excess ammonia present in the distribution system. Nitrification can have adverse effects on water quality, including a loss of total chlorine, an increase in heterotrophic plate count bacteria concentration, and potential increases in total coliforms. A violation of the USEPA Disinfection Byproduct Rule (DBPR) and/or Total Coliform Rule may lead to severe customer illness throughout the District. Air temperature in the District is consistently high during summer months averaging 89, 95, 95, and 88 degrees Fahrenheit in June, July, August and September, respectively. Higher temperatures significantly increase the temperature of water already in the tanks. The groundwater, which enters the bottom of the tank, is much cooler, resulting in the hot, less dense water stagnating at the top. The stagnant hot water in the tank tends to have long residence times, promoting growth of bacteria and formation of disinfection by-products. Disinfection byproduct samples are not collected within the tanks; however, samples in the distribution system were taken under the Stage 1 DBPR. Between February 2004 and July 2008, the District collected 564 Total Trihalomethanes (TTHM) samples, which is one of the disinfection byproducts required to be monitored under the Stage 1 DBPR. These samples were gathered from the District’s Lancaster and Desert View Highlands water system. The TTHM levels ranged from 0.0 parts per billion (ppb) to 166.0 ppb and were above the Maximum Contaminant Level of 80 ppb 103 times during this period. In addition, the water provided by AVEK has continuously been increasing in TTHM levels. For example, in July 2008, AVEK provided the District with water containing 119 ppb of TTHMs. | 52500 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910070-032 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Arsenic Treatment in Well 4-84 | This project will reduce arsenic levels from the groundwater pumped from Well No. 4-84 ensuring compliance with the new arsenic standard of 10 ppb. To accomplish this goal, the District proposes using one of the commercially available ion exchange systems for arsenic treatment. Ion exchange is designated as the Best Available Technology by the US EPA for the removal of arsenic from drinking water sources. Several ion exchange treatment systems have already been permitted by the California Department of Public Health and are in operation in the State. A typical ion exchange treatment system is simple, robust, compact, easy to automate, and can be operated on demand. The treatment goal is to reduce the arsenic in the effluent (treated) water to less than 4 ppb. The proposed packaged wellhead arsenic removal system includes a treatment module, pre-filter assembly, salt/saturator tank, brine processing unit, and brine wastewater storage tank(s). Details of each component that is sized to treat the flow rate from Well No. 4-84 at 500 GPM are as follows. The treatment module (i.e., ion exchange system) uses multiple columns of ion exchange resin operating in parallel to remove the arsenic from the well water. The columns are installed in a 8’W x20’L x 9’H mobile container, eliminating the need for a building or other housing structures. The ion exchange resin is regenerated using a sodium chloride (salt) solution. The treatment module is equipped with a pre-filter assembly consisting of canisters with easy removable lids that allow for the quick replacement of filter elements. The filter assembly’s purpose is to collect large particulate matter before it enters the ion exchange beds keeping them from fouling up and eliminating the need for backwash. A salt storage container (6,800 gallons) is installed to function as the saturator where the concentrated salt/water solution is produced for the onsite regeneration of the ion exchange resin. A brine processing unit (10’W x 20’L x 9’H) is designed for processing the brine wastewater produced from the onsite regeneration of the ion exchange resin. This process employs a precipitation step that binds the arsenic and renders the brine non-hazardous. It also employs a filtration process that separates the solids from the liquid. Two 3,000 gallon tanks for the storage of the spent brine wastewater are installed. The estimated total cost of the above treatment system is $499,272. | G | C | This project targets arsenic contamination in drinking water. Arsenic has been shown to negatively impact human health and is considered one of the primary causes of cancer in the world. The Safe Drinking Water Act Amendment of 1996 required the United States Environmental Protection Agency (USEPA) to establish a new drinking water standard for arsenic. In January 2001, the USEPA adopted a new arsenic standard of 10 parts per billion (ppb). The new standard became effective in January 2006.The Los Angeles County Waterworks District No. 40, Antelope Valley, Regions 4 & 34, Lancaster and Desert View Highlands (Regions), serves approximately 145,000 people through over 47,000 service connections in the Lancaster and Palmdale areas of the Antelope Valley. During 2007, groundwater made up approximately 39 percent of the water supply in the Regions. The groundwater is extracted from 33 wells drilled into the aquifers in the Lancaster Subunit of the Antelope Valley Groundwater Basin which is impacted by arsenic found naturally in rocks and minerals. In order to increase water supply reliability, the District recently drilled Well No. 4-84 at South East corner of Avenue H-8 and 5th street East, Lancaster. This well is projected to provide water at the rate of 500 gallons per minute (GPM). However, analysis of a water sample collected on March 26, 2008 showed an arsenic concentration of 12.7 ppb, exceeding the new standard by 2.7 ppb. Therefore, the District proposes the following project for Well No. 4-84 to ensure long-term compliance with the arsenic standard and a high quality of water supply for our customers. | 449345 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910070-034 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Improving Water Quality in the M8-75W Tanks | The purpose of the proposed project is to thoroughly mix the water in the tank to eliminate temperature stratification and stagnant water conditions, which will provide a uniform short water age. To accomplish this goal, the District proposes using one of the commercially available tank mixing devices. The mixing device has little to no energy cost and requires virtually no maintenance, since it is powered by a solar panel placed on the top of the tank. This system efficiently mixes all the water in the tanks by creating a near-laminar flow pattern, which will reach and eliminate all the dead spots. The device will also be equipped with Supervisory Control and Data Acquisition (SCADA) output signals that allow for real-time monitoring of the tank and a chlorine injection system that will help maintain appropriate disinfectant levels in the tank.This mixing device, which consists of three floats in triangular pattern with total float buoyancy of 600 pounds, floats on the water surface with a down intake hose to draw water. The variable length hose automatically adjusts for peak performance at any water depth. The intake remains stationary just above and in contact with the bottom of the tank, preventing the mixer from moving out of place or rotating. This device is capable of pumping about 10,000 gallons per minute for mixing. By using this mixing device, fewer chemicals will be needed when boosting and TTHM formation will be reduced. In addition, this mixing device reduces residual chlorine loss and nitrification, reduces water treatment costs, ensures compliance with the Disinfection Byproduct Rule and/or Total Coliform Rule, and enables the District to provide high quality water for its customers.Through the Proposition 50 grant funding from the State, a solarbee tank mixer was recently installed in the 0.5 million gallon Cuyama Tank within the District’s Lake Los Angeles water system. Before installation of the mixer on July 24, 2008, the water temperature in the tank varied by 8.1 degrees Fahrenheit from the surface to six meters in depth. The temperature difference was reduced to 3.7 degrees Fahrenheit after only one day of tank mixing, proving that the mixer effectively eliminated thermal stratification and provided uniform, short water age.The estimated total capital cost of the mixing device is $80,000. | G | C | Los Angeles County Waterworks District No. 40 receives its water from the Antelope Valley-East Kern Water Agency (AVEK) and the District’s wells in the Antelope Valley. AVEK currently disinfects with chlorine but plans to switch to chloramines in 2009. Within the District, the two M8-75W tanks located at 41610 75th Street West have a storage capacity of 1,700,000 and 3,000,000 gallons. The tanks currently have a common inlet/outlet connection. This connection is sized for throughput capacity at minimum head loss, which results in a very low flow velocity into the tank during filling. This low velocity results in poor mixing within the tanks, leading to stagnation. In addition, the freshest water added to the tank is the first to be drawn out. This process leads to thermal stratification within the tank since fresh cold water stays near the base and warmer, older water stagnates near the top. Long storage times and lack of mixing water in the storage facilities promotes formation of disinfection byproducts that may cause liver, kidney, or central nervous system problems and may increase the risk of cancer. Once chloramination begins in 2009, the situation is likely to foster nitrification that occurs when the chloraminated water has excess ammonia present in the distribution system. Nitrification can have adverse effects on water quality, including a loss of total chlorine, an increase in heterotrophic plate count bacteria concentration, and potential increases in total coliforms. A violation of the USEPA Disinfection Byproduct Rule (DBPR) and/or Total Coliform Rule may lead to severe customer illness throughout the District. Air temperature in the District is consistently high during summer months averaging 89, 95, 95, and 88 degrees Fahrenheit in June, July, August and September, respectively. Higher temperatures significantly increase the temperature of water already in the tanks. The groundwater, which enters the bottom of the tank, is much cooler, resulting in the hot, less dense water stagnating at the top. Temperature measurements were taken at different depths within the tanks during August 2008. The temperature readings were 85 and 80 degrees Fahrenheit at the top and bottom, respectively. The 5 degree difference in temperature at different depths indicates uneven mixing, increasing the potential for stagnant areas to form, promoting the formation of disinfection by-products.Disinfection byproduct samples are not collected within the tanks; however, samples in the distribution system were taken under the Stage 1 DBPR. Between February 2004 and July 2008, the District collected 564 Total Trihalomethanes (TTHM) samples, which is one of the disinfection byproducts required to be monitored under the Stage 1 DBPR. These samples were gathered from the District’s Lancaster and Desert View Highlands water system. The TTHM levels ranged from 0.0 parts per billion (ppb) to 166.0 ppb and were above the Maximum Contaminant Level of 80 ppb 103 times during this period. In addition, the water provided by AVEK has continuously been increasing in TTHM levels. For example, in July 2008, AVEK provided the District with water containing 119 ppb of TTHMs. | 40000 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910070-036 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Improving Water Quality in the City Ranch North Tanks | The purpose of the proposed project is to thoroughly mix the water in the tank to eliminate temperature stratification and stagnant water conditions, which will provide a uniform short water age. To accomplish this goal, the District proposes using one of the commercially available active tank mixing devices. The mixing device has little to no energy cost and requires virtually no maintenance, since it is powered by a solar panel placed on the top of the tank. This system efficiently mixes all the water in the tank by creating a near-laminar flow pattern, which will reach and eliminate all the dead spots. The device will also be equipped with Supervisory Control and Data Acquisition (SCADA) output signals that allow for real-time monitoring of the tank and a chlorine injection system that helps maintain appropriate disinfectant levels in the tank.This mixing device, which consists of three floats in triangular pattern with total float buoyancy of 600 pounds, floats on the water surface with a down intake hose to draw water. The variable length hose automatically adjusts for peak performance at any water depth. The intake remains stationary just above and in contact with the bottom of the tank, preventing the machine from moving out of place or rotating. The proposed system is capable of pumping about 10,000 gallons per minute for mixing. By using this mixing device, fewer chemicals are needed when boosting and TTHM formation will be reduced.. In addition, this mixing device reduces residual chlorine loss and nitrification, reduces water treatment costs, ensures compliance with the Disinfection Byproduct Rule and/or Total Coliform Rule, and enables the District to provide high quality water for its customers.Through the Proposition 50 grant funding from the State, a solarbee tank mixer was recently installed in the 0.5 million gallon Cuyama Tank within the District’s Lake Los Angeles water system. Before installation of the mixer on July 24, 2008, the water temperature in the tank varied by 8.1 degree Fahrenheit from the surface to six meters in depth. The temperature difference was reduced to 3.7 degrees Fahrenheit after only one day of tank mixing, proving that the mixer effectively eliminated thermal stratification and provided uniform, short water age.The estimated total capital cost of the mixing device is $80,000. | G | C | Los Angeles County Waterworks District No. 40 receives its water from Antelope Valley-East Kern Water Agency (AVEK) and the District’s wells in the Antelope Valley. AVEK currently disinfects with chlorine but plans to switch to chloramines in 2009. Within the District, two City Ranch North tanks located at 3002 W. Avenue P12 have a storage capacity of 2,500,000 and 1,500,000 gallons. The tanks have a common inlet/outlet connection. This connection is sized for throughput capacity at minimum head loss, resulting in a very low flow velocity into the tank during filling. This low velocity results in poor mixing within the tanks, leading to stagnation. In addition, the freshest water added to the tank is the first to be drawn out. This process leads to thermal stratification within the tanks since fresh cold water stays near the base and warmer, older water stagnates near the top. Long storage times and the lack of mixing water in the tanks promotes formation of disinfection byproducts that may cause liver, kidney, or central nervous system problems and may increase the risk of cancer. Once chloramination begins in 2009, the situation is likely to foster nitrification that occurs when the chloraminated water has excess ammonia present in the distribution system. Nitrification can have adverse effects on water quality, including a loss of total chlorine, an increase in heterotrophic plate count bacteria concentration, and potential increases in total coliforms. A violation of the USEPA Disinfection Byproduct Rule and/or Total Coliform Rule may lead to severe customer illness throughout the District. Air temperature in the District is consistently high during summer months, averaging 89, 95, 95, and 88 degrees Fahrenheit in June, July, August and September, respectively. Higher temperatures significantly increase the temperature of water already in the tanks. The groundwater, which enters the bottom of the tank, is much cooler, resulting in the hot, less dense water stagnating at the top. Temperature measurements were taken at different depths within the tanks during August 2008. The temperature readings were 84.2 and 79.0 degrees Fahrenheit at the top and bottom, respectively. The 5.2 degree difference at different depths indicates uneven mixing, increasing the potential for stagnant areas to form, promoting the formation of disinfection by-products.Disinfection byproduct samples are not collected within the tanks; however, samples in the distribution system were taken under the Stage 1 DBPR. Between February 2004 and July 2008, the District collected 564 Total Trihalomethanes (TTHM) samples, which is one of the disinfection byproducts required to be monitored under the Stage 1 DBPR, between February 2004 and July 2008 within the District’s Lancaster and Desert View Highlands water system. The TTHM levels ranged from 0.0 ppb to 166.0 ppb and were above the Maximum Contaminant Level of 80 parts per billion (ppb) 103 times during this period. In addition, the water provided by AVEK has continuously been increasing in TTHM levels. For example, in July 2008, AVEK provided the District with water containing 119 ppb of TTHMs. | 40000 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910070-033 | 1910070 | LOS ANGELES CO WW DIST 4 & 34-LANCASTER | Arsenic treatment in Well 4-82 | This project will reduce arsenic levels from the groundwater pumped from Well No. 4-82 ensuring compliance with the new arsenic standard of 10 ppb. To accomplish this goal, the District proposes using one of the commercially available ion exchange systems for arsenic treatment. Ion exchange is designated as the Best Available Technology by the US EPA for the removal of arsenic from drinking water sources. Several ion exchange treatment systems have already been permitted by the California Department of Public Health and are in operation in the State. A typical ion exchange treatment system is simple, robust, compact, easy to automate, and can be operated on demand. The treatment goal is to reduce the arsenic in the effluent (treated) water to less than 4 ppb. The proposed packaged wellhead arsenic removal system includes a treatment module, pre-filter assembly, salt/saturator tank, brine processing unit, and brine wastewater storage tank(s). Details of each component that is sized to treat the flow rate from Well No. 4-82 at 500 GPM are as follows. The treatment module (i.e., ion exchange system) uses multiple columns of ion exchange resin operating in parallel to remove the arsenic from the well water. The columns are installed in a 8’W x20’L x 9’H mobile container, eliminating the need for a building or other housing structures. The ion exchange resin is regenerated using a sodium chloride (salt) solution. The treatment module is equipped with a pre-filter assembly consisting of canisters with easy removable lids that allow for the quick replacement of filter elements. The filter assembly’s purpose is to collect large particulate matter before it enters the ion exchange beds keeping them from fouling up and eliminating the need for backwash. A salt storage container (6,800 gallons) is installed to function as the saturator where the concentrated salt/water solution is produced for the onsite regeneration of the ion exchange resin. A brine processing unit (10’W x 20’L x 9’H) is designed for processing the brine wastewater produced from the onsite regeneration of the ion exchange resin. This process employs a precipitation step that binds the arsenic and renders the brine non-hazardous. It also employs a filtration process that separates the solids from the liquid. Two 3,000 gallon tanks for the storage of the spent brine wastewater are installed. The estimated total cost of the above treatment system is $499,272 | G | C | This project targets arsenic contamination in drinking water. Arsenic has been shown to negatively impact human health and is considered one of the primary causes of cancer in the world. The Safe Drinking Water Act Amendment of 1996 required the United States Environmental Protection Agency (USEPA) to establish a new drinking water standard for arsenic. In January 2001, the USEPA adopted a new arsenic standard of 10 parts per billion (ppb). The new standard became effective in January 2006.The Los Angeles County Waterworks District No. 40, Antelope Valley, Regions 4 & 34, Lancaster and Desert View Highlands (Regions), serves approximately 145,000 people through over 47,000 service connections in the Lancaster and Palmdale areas of the Antelope Valley. During 2007, groundwater made up approximately 39 percent of the water supply in the Regions. The groundwater is extracted from 33 wells drilled into the aquifers in the Lancaster Subunit of the Antelope Valley Groundwater Basin which is impacted by arsenic found naturally in rocks and minerals. In order to increase water supply reliability, the District recently drilled Well No. 4-82 at 419 West Avenue J, Lancaster. This well is projected to provide water at the rate of 500 gallons per minute (GPM). However, analysis of a water sample collected on February 5, 2008 showed an arsenic concentration of 14.9 ppb, exceeding the new standard by 4.9 ppb. Therefore, the District proposes the following project for Well No. 4-82 to ensure long-term compliance with the arsenic standard and a high quality of water supply for our customers. | 449345 | 46878 | 144215 | 16 | Los Angeles | IV | 2008
1910067-051 | 1910067 | LOS ANGELES-CITY, DEPT. OF WATER & POWER | Tank & Reservoir Nitrification Control Plan | The project includes the installation of mixers in some 30 – 40 priority storage tanks and reservoirs to allow fro easier treatment of the water should nitrification begin in these facilities. Also additional on-line analyzers will be installed at numerous locations to monitor the total chlorine level to prevent having to breakpoint chlorinate the water which would produce disinfection byproducts. An additional step may include the development and installation of ultraviolet blacklights in a number of tanks and reservoirs to inhibit the effect of nitrifying bacteria in the water. | G | C | The LADWP has determined that it must change from a free chlorine residual disinfectant in the water distribution system to a chloramine disinfectant in order to meet the Stage 2 Disinfectant/Disinfection Byproducts Rule. When this change occurs there are approximately 30-40 priority tanks and reservoirs which have longer than 5 day residence times and will therefore be prone to nitrification due to the presence of ammonia in the water. | 3636177 | 686422 | 4071873 | 15 | Los Angeles | IV | 2012
0500095-001 | 0500095 | FOOTHILL COMMUNITY CHURCH | Foothill Community Church - Water System Treatment Project | Installation of treatment facilities is the most cost efficient method to provide potable water consistent with Calaveras County Environmental Health Department (CCEHD) requirements. Project implementation requires engineering design, compliance with CEQA, preparation of construction plans and specifications, and construction of treatment facilities and appurtenances.Consolidation was considered; however, preliminary cost estimates indicate probable costs of approximately $1.1 million to connect to the nearest water utility providers. The estimated cost to design and construct treatment facilities is $250,000 making this the most feasible alternative.The proposed scope of construction work includes earthwork, replacement of the existing water storage tank, installation of a reverse osmosis or other adequate treatment system, on site piping modifications, electrical work, and installation of wastewater (backwash) storage facilities. Installation of treatment facilities will require increased O&M personnel with appropriate State licensing. Long-term operation and maintenance (O&M) cost increases will be borne by the Church. | G | P | The Foothill Community Church Water System provides water to a church complex consisting of the church facilities, the school facilities, and the pastor’s private residence.Water is obtained from a drilled well (Well 01) that is 600 feet deep and has a yield of approximately 60 gpm. Water is pumped to a 22,750 gallon, galvanized steel storage tank. A booster pump pressurizes a 1,500 gallon, quarter inch, epoxy coated, steel pressure tank.Water from Well 01 is characterized by high levels of salts, boron, and pH. The water is corrosive and toxic to plant life.Test results for Well 01 indicate elevated levels of salts, high pH, and elevated levels of fluoride that exceed Primary Drinking Water Standards of 2.0 ug/L. Water from Well 01 also exceed recommended levels for Secondary Drinking Water Standards for Total Dissolved Solids and Specific Conductance. The observed levels of Boron in water from Well 01 exceed both the State Action Level of 1,000 ug/L and United State Environmental Protection Agency Health Advisory level of 600 ug/L. Contaminants of concern and their concentrations are as follows:Fluoride 2.5 ug/L (7/30/06) 2.2 ug/L (7/18/12)pH 8.7 units (7/31/03)TDS 1070 mg/L (7/31/03)Specific Conductance 1580 umho/cm (7/31/03)Sodium 348 mg/L (7/31/03)Boron 5.6 mg/L (7/31/03)Well 03 was completed on April 30, 2003 to mitigate the substandard water supply from Well 01. Well 03 yielded 18-20 gpm and, like Well 01, water from Well 03 is toxic to plant life. Well 03 was found to have elevated levels of Antimony, Arsenic, and Fluoride that exceeded Primary Drinking Water Standards. The concentration of Thallium nearly equaled the MCL. Well 03 was removed from service and Well 01 was returned to service. The system relies on bottled water for human consumption and uses well water for sanitation purposes. Pursuant to Calaveras County Environmental Health Department (CCEHD), the use of bottled water is allowed in emergency situations for limited periods of time only, and the long term reliance on bottled water is not an acceptable substitute for an adequate supply of pure, wholesome, healthful, and potable water. CCEHD issued Compliance Order 05 00 004, 03-01-13A on March 29, 2013 requiring an engineering report and installation of approved water treatment technology. The requested funding would allow design and construction of a treatment system. CCEDH finds that the System is in violation of:§116555(a)(1), Article 7, Part 12 of the California Health and Safety Code for failing to comply with primary and secondary drinking water standards.§116555(a)(3), Article 7, Part 12 of the California Health and Safety Code for failing to provide a reliable and adequate supply of pure, wholesome, healthful, and potable water.§64431, Article 4, Chapter 15 of Title 22 California Code of Regulations for exceeding the Maximum Allowable Contaminant Level (MCL) for Fluoride.§64449, Article 16, Chapter 15 of Title 22 California Code of Regulations for exceeding Maximum Allowable Contaminant Level (MCL) for Secondary Drinking Water Standards. | 250000 | 2 | 85 | 10 | Calaveras | III | 2013
3600184-001 | 3600184 | North Shore MWC | Uranium Treatment | Study, design, engineer, and install a treatment system to reduce uranium level below MCL. | G | S | Exceeds the MCL for uranium | 150000 | 0 | 0 | 13 | San Bernardino | V | 2012
2000551-004 | 2000551 | MD#07 MARINA VIEW HEIGHTS | Water Meter Installation | The project would entail installation of water meters at each service connection to promote water conservation. The addition of meters will allow the system to establish a tiered water rate to generate revenues to maintain and upgrade the system's facilities and infrastructures. | H | C | The current water system does not include water meters, leading to increased water usage by the customers. The current system serves 92 connections. | 184000 | 74 | 200 | 11 | Madera | III | 2009
5410004-001 | 5410004 | Farmersville, City of | Farmersville Water Meter Installation | The City of Farmersville proposes to install 2717 water meters in order to create a 100% metered water distribution system. The current system only provides water on a flat rate basis. The project falls under Category H in the Project Priority List, “water systems which do not provide meters for the water delivered to customers.” In order to achieve this goal, the City will utilize its standard procurement process to obtain bids and select the best purveyor to provide the most appropriate meters, software, and other necessary equipment. Preliminary estimates have been provided by numerous manufacturers. A final implementation schedule will be prepared and environmental clearance will be obtained by June 2009. It is anticipated that the project will be categorically exempt from NEPA and CEQA, because in all cases the meters will be installed at previously disturbed sites. The project will be ready for implementation by August 2009 and complete within 1 year from the actual start date.Equipment costs are estimated at $624,470. Equipment needed includes:• 1600 3/4” water meters, • 1100 1” water meters• 6 1 ½” water meters• 11 2” water meters• 1 Radio Read hand-held devise and related software Labor costs for installation are estimated at $37,530 which includes 1,390 hours at a rate of $27 per hour. In obtaining initial estimates for this project, City staff has found it to be most cost effective to implement this project as comprehensively and quickly as possibly rather than a phased, gradual implementation of the meter system over the course of several years. This practice will enable the City of Farmersville to stay “ahead of the curve” in complying with the read and charge regulations that will eventually apply to all customers served. The City did consider installing only 788 meters to structures built after 1992. These structures are the first which will be required to have metered water usage by January 1, 2010. However, after noting a significant cost savings in planning for city-wide implementation within one year of this funding award, it was determined that this indeed was the best course of action to efficiently and effectively help Farmersville reach its goal of transitioning from a 100% flat rate water distribution system to a 100% metered system. | H | C | The City of Farmersville serves a disadvantaged population of approximately 10,500 residents. The median household income in Farmersville in 2007 was $33,068. (www.city-data.com) The City is not supported by a strong retail tax base, and as a result, at times, struggles to provide even basic services to its residents due to financial constraints. The City’s Public Works Department provides water to approximately 2700 households and structures. At this time, all of the water is provided on a flat rate basis. This is due, in large part, to the fact that the great majority of existing meters in Farmersville are more than 20 years old, non-functional, (broken dials) and have reached the end of their useful life. Flat rate billing for water service is simply the only option for Farmersville at this time. State law will require approximately one third of Farmersville water customers to be metered by the end of this year. All of the City’s water customers will need meters by 2025. Empirical evidence has proven that flat rate water billing encourages excessive and wasteful water use, since the customer has no knowledge of exorbitant use or the financial cost associated with it. Installing current technology would enable the City to accurately and efficiently read meters and charge accordingly for water usage. The City of Farmersville recognizes that installing new meters will have multi-faceted benefits. These advantages include a greater consciousness of water usage by customers, resulting in water conservation, and accurate billing. The new technology will enable city workers to automatically read digital meters using a remote, drive-by, handheld system. The new meters will also enable the City to comply with California Water Code Section 525-529.7 which will require metered reading to roughly 29% of its customers by January 1, 2010. The entire service area will need to comply with the new “read and charge” code by 2025. This installation does not require public notification, but City staff would create and disseminate bi-lingual correspondence notifying residents of the meter installation prior to the project’s commencement and again prior to actual installation on a street-by-street basis.By addressing this problem in a comprehensive, expedient manner it will enable the City to adhere to its “Best Management Practices”. The transition to a “read and charge” water distribution system will also allow the City to manage water usage, billing, and labor costs. Funding from the Safe Drinking Water State Revolving Fund would enable the City of Farmersville to correct a significant public water system deficiency in a community with demonstrated need. | 662000 | 2374 | 10672 | 12 | Tulare | III | 2009
1610004-006 | 1610004 | Corcoran, City of | Meters for service connections | INSTALL METER SYSTEM WIDE. OTHER - DESIGN AND CONSTRUCTION | H | C | GENERALLY NON-METERED, HOWEVER, NEW DEVELOPMENTS ARE METERED. THE METERED HOMES GREATLY REDUCE WATER USE | 1800000 | 2878 | 26047 | 12 | Kings | III | 1998
3410004-009 | 3410004 | Carmichael Water District | Carmichael Water District La Vista Well and Tank Replacement Project | This project will include planning, design, permitting, environmental compliance, and construction of replacement of Carmichael Water District’s (District) existing aging La Vista groundwater well, storage tank, and booster pump station facility. The new facility will be consistent with the objectives laid out in the Regional Water Authority’s 2005 Integrated Regional Water Management Plan. This project will also better equip the District to address the threat of Aerojet/Gencorp Corporation groundwater contaminant plumes and local plumes through continued efforts to manage groundwater extractions and increase the use of surface water when available. The specific project components are described as follows: Groundwater Well Replacement – The existing La Vista well will be destroyed and redrilled on site. The new well will be selectively screened in layers of the aquifer to minimize the likelihood of future impacts from migration of the Aerojet groundwater contaminant plumes and local Potential Contaminating Activities. The new well will also be used as a long term groundwater source to offset some of the effects the loss of the Barrett Road Well in the north part of the district to contamination. The reconstruction of the La Vista well will improve the District’s reliable source water production capacity.  4 Million Gallon (MG) Storage Tank and Booster Pump Station - This project will include demolition of the existing above ground welded steel water storage tank and construction of a new 4 MG above ground welded steel tank and booster pump station. Structural inspections have indicated that the existing storage tank is severely corroded and subject to near-term failure. In 2007, the tank was converted to provide the capability to store surface water in addition to groundwater from the La Vista well. The surface water storage capability provides additional surface water peaking capacity and reduces the District’s reliance on groundwater pumping. This effort has been successful, but replacement of the facility is needed. | H | C | To date, five of the eight Carmichael Water District (District) groundwater supply wells have been impacted by contamination from multiple sources, primarily perchlorate and Tetrachlorethylene (PCE). Other contaminants, including n-nitrosodimethylamine (NDMA), trichlorethylne (TCE), and 1,4 dioxane are known to be present in the aquifer underlying District and also present long term threats to the sustainability of a high quality groundwater source. The primary known source of contamination in the District service area is from historical activities at Gencorp/Aerojet Corporation’s (Aerojet’s) aerospace and rocket engine manufacturing facility. The Aerojet plume is a Superfund site administered cooperatively by the USEPA, California Department of Toxic Substances Control, and the Central Valley Regional Water Quality Control Board. There have been ongoing remediation efforts within the District’s service area, however the contaminant plume is still not fully contained and is migrating westerly towards the District’s groundwater wells at an estimated rate of 500 feet per year. Following is a description of the contaminants that currently impact District supply sources: Over the past 5 years, perchlorate has been detected in three (3) of the District’s wells over a range of approximately 1 to 4 parts per billion (ppb), approaching the California Maximum Contaminant Level (MCL). The perchlorate is possibly associated with the Aerojet contaminant plumes; although a definitive hydraulic connection has not been confirmed.  Tetrachlorethylene (PCE) has been detected in 5 (five) wells. One of the District’s wells (Barrett Road Well) has been removed from service due to PCE concentrations in excess of the MCL. The PCE and other possible future chemicals associated with potentially contaminating activities (PCA’s) were identified in the District’s 2003 Drinking Water Source Assessment Program. Review of known PCA’s indicates that additional wells may be susceptible to PCA’s including: dry cleaners, leaking underground fuel tanks, automobile repair and machine shops, and facilities involved in fertilizer manufacture and application. The District practices conjunctive use of surface water and groundwater and during summer months when high system demands occur, relies substantially on its wells to supplement the production capacity of the surface water treatment plant (WTP). The loss of any additional groundwater facilities could jeopardize the District’s ability to maintain adequate distribution system pressures without implementing emergency conservation measures. This project would provide a replacement groundwater source, and other water transmission and storage improvements to enable the District to continue to provide high quality groundwater and maximize the use of surface water. These efforts will help to achieve a net reduction in groundwater pumping and support collaboration with Aerojet and other down gradient water agencies (including Del Paso Manor Water District and Sacramento Suburban Water District) by improving flexibility in conjunctive supply options and protect against the impact of additional public water supply losses. | 5000000 | 11548 | 40000 | 09 | Sacramento | I | 2009
0910001-015 | 0910001 | El Dorado ID - Main | El Dorado Irrigation District | (Res B) Replace floating cover with rigid cover and an adequate bypass. Involves design and construction. | H | C | Reservoir is covered with a floating cover which is defective. | 800000 | 36244 | 112000 | 09 | El Dorado | I | 2006
0910001-012 | 0910001 | El Dorado ID - Main | El Dorado Irrigation District | (Moose Hall) Replace floating cover with a rigid cover and an adequate bypass. Involves design and construction. | H | C | Reservoir is protected with a floating cover, which has defects. | 600000 | 36244 | 112000 | 09 | El Dorado | I | 2006
0910001-013 | 0910001 | El Dorado ID - Main | El Dorado Irrigation District | (Dolomite) Replace floating cover with rigid cover. Involves design and construction. | H | C | Reservoir is covered with a floating cover, which has defects. | 2300000 | 36244 | 112000 | 09 | El Dorado | I | 2006
0910001-017 | 0910001 | El Dorado ID - Main | El Dorado Irrigation District | (Res 1) Replace floating cover with a rigid cover and an adequate bypass. Involves design and construction. | H | C | Reservoir is covered with a floating cover which is defective. | 1700000 | 36244 | 112000 | 09 | El Dorado | I | 2006
0910001-016 | 0910001 | El Dorado ID - Main | El Dorado Irrigation District | (Res C) Replace floating cover with a rigid cover and an adequate bypass. Involves design and construction. | H | C | Reservoir is covered with a floating cover which is defective. | 800000 | 36244 | 112000 | 09 | El Dorado | I | 2006
0910001-024 | 0910001 | El Dorado ID - Main | Pollock Pines Reservoir Floating Cover Replacement | Replace the existing floating covered reservoir with two steel storage tanks, with a total volume of 3.5 million gallons. | H | C | The District is currently under Compliance Order No. 01-09-98-ORD-001, Amendment No. 5 dated June 6, 2005. A prior amendment (No.3) required the District to "abandon the use of all existing uncovered and floating covered drinking water reservoirs and construct new, covered drinking water storage facilities" | 4500000 | 36244 | 112000 | 09 | El Dorado | I | 2009
0910001-029 | 0910001 | El Dorado ID - Main | Reservoir 11 Floating Cover Replacement | Replace the existing floating covered reservoir with two steel storage tanks, with a total volume of 5.0 million gallons. | H | C | The District is currently under Compliance Order No. 01-09-98-ORD-001, Amendment No. 5 dated June 6, 2005. A prior amendment (No.3) required the District to "abandon the use of all existing uncovered and floating covered drinking water reservoirs and construct new, covered drinking water storage facilities" | 6140000 | 36244 | 112000 | 09 | El Dorado | I | 2009
4400598-001 | 4400598 | PURESOURCE WATER, INC | Water Meter Installation | The project is to physically locate all 79 service connections at the curb stop, then install “drive by” remote meters, curb stops, meter boxes and lids, plus the meter-reading equipment and software.This will permit the use of tiered rates and thus encourage water conservation. During periods of restricted usage, it will provide a means of monitoring use and of any violation of use restrictions. It will also permit leak detection for individual consumers and for the system as a whole. | H | C | Currrently the system is un-metered and only flat-rate service is offered. Project is to install drive-by remote-read meters all necessary at all service connections and appropriate billing and record-keeping software, etc. This is to comply with CDPH and CPUC, as well as Federal efforts to reduce water consumption. | 70000 | 79 | 450 | 05 | Santa Cruz | II | 2009
3410020-033 | 3410020 | City of Sacramento | Complete metering of water system | Meter project | H | C | Meter project is necessary to meet the requirements of Assembly Bill 2572 by installing water meters on existing water services within the Cityof Sacramento. This law set a deadline of 100% metering of all residential and commercial accounts by 2015 | 5000000 | 137886 | 407018 | 09 | Sacramento | I | 2010
1910067-044 | 1910067 | LOS ANGELES-CITY, DEPT. OF WATER & POWER | Lower Franklin Reservoir Floating Cover - Replacement | This project removes the existing cover and designs and installs a new floating cover. The project includes modification to the inlet and outlet structures to provide better cover fit and performance. The project would also install reservoir perimeter fire hydrant system to provide wash down capability for improved maintenance. | H | C | The floating cover at Lower Franklin Reservoir is well beyond its 20 year design life. Maintenance of the cover has become increasingly more difficult as the Hypalon material has degraded to a point that the integrity cannot be maintained by patching. The cover must be replaced in order to maintain water quality standards that protect public health, and to meet State Waterworks regulations which require that all distribution reservoirs be covered. The reservoir was recently inspected by the California Department of Public, Health Drinking Water Program and it was recommended that the cover be replaced as soon as possible. While recent budgetary reductions have pushed this project out 10 years, estimate will be revised to reflect accelerated project schedule. | 6884127 | 686422 | 4071873 | 15 | Los Angeles | IV | 2012
1910067-045 | 1910067 | LOS ANGELES-CITY, DEPT. OF WATER & POWER | Green Verdugo Reservoir Floating Cover - Replacement | This project removes the existing cover and designs and installs a new floating cover. The project includes modification to the inlet and outlet structures to provide better cover fit and performance. The project would also modify the mixer location to improve chloramine treatment. | H | C | The floating cover at Green Verdugo Reservoir is beyond its 20 year design life. The cover must be replaced in order to maintain water quality standards that protect public health, and to meet State Waterworks regulations which require that all distribution reservoirs be covered. The reservoir was recently inspected by the California Department of Public Health, Drinking Water Program and it was recommended that the design of the new floating cover begin as soon as possible. While recent budgetary reductions have pushed this project out 10 years, estimate will be revised to reflect accelerated project schedule. | 124178781 | 686422 | 4071873 | 15 | Los Angeles | IV | 2012