Infeasibility Evaluation and Calculation of Performance Based Effluent Limits – Crockett Cogeneration, LLP

## A. INTRODUCTION

This report documents the infeasibility analysis and performance based effluent limits (PBELs) calculations the Water Board staff has conducted for reissuance of Crockett Cogeneration’s NPDES permit.  The analysis is based on evaluating the frequency distribution of Crockett Cogeneration’s last three years of effluent data (June 2000 to July 2003), including non-detect measurements.  The statistical software MiniTab (and macro MDLNORM by Dr. Hesel) was used to determine statistical results.

Nine pollutants are analyzed here because they demonstrate reasonable potential (RP), as discussed in a separate analysis (see the RPA spreadsheet, “CrockettCo_RPA.xls”).  RP was triggerred either because the maximum effluent concentration (MEC) exceeded the minimum water quality objective (WQO), or the maximum background concentration exceeded the maximum background concentration (B):

| Constituent | WQO/WQC (µg/L) | Basis1 | MEC (µg/L) | Maximum Ambient Background Conc. (µg/L) | Reason for Reasonable Potential |
| --- | --- | --- | --- | --- | --- |
| 1) Copper | 3.74 | CTR | 26 | 2.45 | MEC>C |
| 2) Lead | 5.6 | BP | 29 | 0.8 | MEC>C |
| 3) Nickel | 7.1 | BP | 67 | 3.7 | MEC>C |
| 4) Selenium | 5 | CTR | 8 | 0.39 | MEC>C |
| 5) Zinc | 58 | BP | 120 | 4.4 | MEC>C |
| 6) Cyanide | 1 | CTR | 14 | <0.4 | MEC>C |
| 7) 4,4'-DDE | 0.000000014 | CTR | <0.637 | 0.000000071 | B>C |
| 8) Dioxin-TEQ (2,3,7,8 TCDD) | 0.00059 | CTR | <0.001 | 0.000693 | B>C |
| 9) Dieldrin | 0.00014 | CTR | <0.002 | 0.000264 | B>C |

1.  CTR = California Toxic Rule; BP = Basin Plan

B. METHOD

The four steps used in the infeasibility analyses and PBEL calculations are described below:

- Which frequency distribution model does effluent data most accurately follow—Normal or Log-Normal?

The best distribution was evaluated by considering the following criteria, and using best judgement:
a) Which AD (Anderson Darling coefficient) is lowest? (< 1.01?)

b) Which P-value is greatest ?  (> 0.05?)

c) Which symmetry plot best follows a straight line?

If there are not enough measurements to make an accurate evaluation, based on best professional judement, a log-normal distribution is assumed because this is consistent with distributions for most pollutants, and because log-normal distributions are less likely than normal distributions to under-estimate PBEL’s.

2.  Determine Mean, 95th and 99th Percentile of Effluent Data

- For Normal Distribution:  	
 95th Percentile = Mean + 1.645 * SD     (where SD is Standard Deviation)
99th Percentile = Mean + 2.326 * SD

- For Log-Normal Distribution:
 95th Percentile = exp (Transformed_Mean + 1.6545 Transformed_SD)
 99th Percentile = exp (Transformed_Mean + 2.326 * Transformed_SD)

3.  Is it feasible for discharger to comply with Average Monthly Effluent Limit (AMEL) and Maximum Daily Effluent Limit (MDEL)?

If any one or more of the following three conditions exist, then infeasibility is concluded:
a)  95th Percentile > AMEL
b)  99th Percentile > MDEL
c)  Mean of Non-Transformed Data > Long Term Average (LTA)

(Mean of non-transformed data is compared to LTA, since it is the best estimate of a true average.  Converting the transformed mean back to the original scale will not accurately estimate the true average, because of transformation bias.)

4. Determine Performance Based Effluent Limits (PBELs) if enough data

If infeasibility is concluded, set PBEL to the 99.87th Percentile of effluent data:

- For normal distribution:  
   PBEL = Mean + 3 * SD

- For log-normal distirubtion:  
   PBEL = exp(Transformed_Mean + 3 * Transformed_SD)

C.  SUMMARY

The following table summarizes the feasibility determinations and PBELs for each pollutant (all units in micrograms per liter).  For seven of the nine pollutants, it was found there is a significant statistical likelihood the Discharger will not be able to immediately comply with the final water quality based effluent limitations (WQBELs), based on recent plant performance, or due to uncertainty associated with the large magnitude of the available method detection limits (MDLs).  For lead and zinc, there is a high statistical likelihood the Discharger can comply with the final WQBELs.  Section D below describes the results of the analyses for each pollutant in greater detail.  (The WQBELs (Average Monthly Efflunet Limits (AMELs) and Maximum Dailiy Effluent Limits (MDELs)), are calculated in the RPA spreadsheet.)

| Pollutant | Mean / LTA | 95th / AMEL | 99th / MDEL | Feasible to comply? | PBEL | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| 1) Copper |  | 28 > 13 | 85 > 25 | No | 251.6 |  |
| 2) Lead | 0.72 < 26 | 7.2 < 40 | 21 < 80 | Yes |  |  |
| 3) Nickel |  |  | 107 > 62 | No | 366.9 |  |
| 4) Selenium |  | 11 > 4.1 | 23 > 8.2 | No | 50.5 |  |
| 5) Zinc | 23 < 196 | 126 < 390 | 820 < 990 | Yes |  |  |
| 6) Cyanide |  | 21 > 3.2 | 74 > 6.4 | No | 19.2 |  |
| 7) Dioxin TEQ (2,3,7,8 TCDD) |  | 0.000000014 | 0.000000028 | No | To be determined | Unable at this time to determine PBEL |
| 8) 4,4'-DDE |  | 0.00059 | 0.00118 | No | 0.05 | PBEL = ML, since minimum effluent MDL > WQO |
| 9) Dieldrin |  | 0.00014 | 0.00028 | No | 0.01 | PBEL = ML, since minimum effluent MDL > WQO |

D. RESULTS

(1) COPPER

Log-Normal Distribution is best model (AD=1.435; P-value=0.320)

Transformed_Mean =  0.686

Transformed_SD =  1.614

95th =  exp(0.686 + 1.645 * 1.614) = 28.2    > AMEL(12.5)

99th =  exp(0.686 + 2.326 * 1.614) = 84.8    > MDEL(25.1)

Infeasibility Concluded Since:

95th > AMEL therefore Infeasible to Comply

99th > MDEL therefore Infeasible to Comply

PBEL = exp(0.686 + 3 * 1.614) = 251.6

MINITAB Results

Descriptive Statistics: ESTIMATE

Variable             N       Mean     Median     TrMean      StDev    SE Mean

ESTIMATE            18      0.686      0.699      0.706      1.614      0.380

Variable       Minimum    Maximum         Q1         Q3

ESTIMATE        -2.207      3.258     -0.584      2.361

| Name | Date | Concentration (µg/L) | MDL (µg/L) | ln(Con) | ln(MDL) |
| --- | --- | --- | --- | --- | --- |
| Copper | 6/1/00 | ND | 5 |  | 1.609 |
| Copper | 7/1/00 | ND | 5 |  | 1.609 |
| Copper | 10/1/00 | ND | 5 |  | 1.609 |
| Copper | 1/1/01 | ND | 5 |  | 1.609 |
| Copper | 4/1/01 | ND | 5 |  | 1.609 |
| Copper | 6/1/01 | 13 |  | 2.565 |  |
| Copper | 8/1/01 | ND | 5 |  | 1.609 |
| Copper | 12/1/01 | ND | 5 |  | 1.609 |
| Copper | 1/1/02 | ND | 5 |  | 1.609 |
| Copper | 03/14/02 | 9.9 |  | 2.293 |  |
| Copper | 04/18/02 | 17 |  | 2.833 |  |
| Copper | 08/12/02 | 2.7 |  | 0.993 |  |
| Copper | 11/20/02 | 1.5 |  | 0.405 |  |
| Copper | 02/04/03 | 3.4 |  | 1.224 |  |
| Copper | 03/05/03 | 26 |  | 3.258 |  |
| Copper | 05/08/03 | 14 |  | 2.639 |  |
| Copper | 06/17/03 | 4.1 |  | 1.411 |  |
| Copper | 07/30/03 | 2.7 |  | 0.993 |  |

(2) LEAD

Log-Normal Distribution Best (AD=1.635; P-value=0.114)

Transformed_Mean =  -0.569

Transformed_SD =  1.546

95th =  exp(-0.569 + 1.645 * 1.546) = 7.2    < AMEL(40.0)

99th =  exp(-0.569 + 2.326 * 1.546) = 20.6  < MDEL(80.2)

Mean of Untransformed Data = 0.72  < LTA(25.7)

Feasibility Concluded Since:

95th < AMEL therefore Feasible to Comply

99th < MDEL therefore Feasible to Comply

Mean < LTA therefore Feasible to Comply

(PBEL = exp(-0.569 + 3 * 1.546) = 251.6)

Descriptive Statistics: ESTIMATE

Variable             N       Mean     Median     TrMean      StDev    SE Mean

ESTIMATE            18     -0.569     -0.696     -0.638      1.546      0.364

Variable       Minimum    Maximum         Q1         Q3

ESTIMATE        -3.390      3.367     -1.481      0.522

| Name | Date | Concentration (µg/L) | MDL (µg/L) | ln(Con) | ln(MDL) |
| --- | --- | --- | --- | --- | --- |
| Lead | 06/01/00 | ND | 5 |  | 1.609 |
| Lead | 07/01/00 | ND | 5 |  | 1.609 |
| Lead | 10/01/00 | ND | 5 |  | 1.609 |
| Lead | 01/01/01 | 29 |  | 3.367 |  |
| Lead | 04/01/01 | ND | 5 |  | 1.609 |
| Lead | 06/01/01 | ND | 5 |  | 1.609 |
| Lead | 08/01/01 | ND | 5 |  | 1.609 |
| Lead | 12/01/01 | ND | 5 |  | 1.609 |
| Lead | 01/01/02 | ND | 5 |  | 1.609 |
| Lead | 03/14/02 | 0.87 |  | -0.139 |  |
| Lead | 04/18/02 | ND | 0.02 |  | -3.912 |
| Lead | 08/12/02 | 0.35 |  | -1.050 |  |
| Lead | 11/20/02 | 0.63 |  | -0.462 |  |
| Lead | 02/04/03 | 0.4 |  | -0.916 |  |
| Lead | 03/05/03 | 0.22 |  | -1.514 |  |
| Lead | 05/08/03 | 2 |  | 0.693 |  |
| Lead | 06/17/03 | 1.8 |  | 0.588 |  |
| Lead | 07/30/03 | 0.23 |  | -1.470 |  |

(3) NICKEL

Log-Normal Distribution Best (AD=1.32; P-value=0.311)

Transformed_Mean =  0.427

Transformed_SD =  1.826

95th =  exp(0.427 + 1.645 * 1.826) = 30.9    > AMEL(30.87)

99th =  exp(0.427 + 2.326 * 1.826) = 107.2  > MDEL(61.9)

Infeasibility Concluded Since:

95th > AMEL therefore Infeasible to Comply

99th > MDEL therefore Infeasible to Comply

PBEL = exp(0.427 + 3 * 1.826) = 366.9

Descriptive Statistics: ESTIMATE

Variable             N       Mean     Median     TrMean      StDev    SE Mean

ESTIMATE            18      0.427      0.587      0.396      1.826      0.430

Variable       Minimum    Maximum         Q1         Q3

ESTIMATE        -2.860      4.205     -1.031      1.970

| Name | Date | Concentration (µg/L) | MDL (µg/L) | ln(Con) | ln(MDL) |
| --- | --- | --- | --- | --- | --- |
| Nickel | 06/01/00 | ND | 5 |  | 1.609 |
| Nickel | 07/01/00 | 14 |  | 2.639 |  |
| Nickel | 10/01/00 | 67 |  | 4.205 |  |
| Nickel | 01/01/01 | ND | 5 |  | 1.609 |
| Nickel | 04/01/01 | ND | 5 |  | 1.609 |
| Nickel | 06/01/01 | ND | 5 |  | 1.609 |
| Nickel | 08/01/01 | ND | 5 |  | 1.609 |
| Nickel | 12/01/01 | ND | 5 |  | 1.609 |
| Nickel | 01/01/02 | ND | 5 |  | 1.609 |
| Nickel | 03/14/02 | 2.7 |  | 0.993 |  |
| Nickel | 04/18/02 | 7.1 |  | 1.960 |  |
| Nickel | 08/12/02 | 2.4 |  | 0.875 |  |
| Nickel | 11/20/02 | 1.3 |  | 0.262 |  |
| Nickel | 02/04/03 | 4.3 |  | 1.459 |  |
| Nickel | 03/05/03 | 7.7 |  | 2.041 |  |
| Nickel | 05/08/03 | 7.4 |  | 2.001 |  |
| Nickel | 06/17/03 | 1.7 |  | 0.531 |  |
| Nickel | 07/30/03 | 1.9 |  | 0.642 |  |

(4) SELENIUM

Log-Normal Distribution Assumed (AD=2.72; P-value=0.301)

(only four detects—will assume selenium is consistent with most other pollutants in being log-normally distributed)

Transformed_Mean =  0.504

Transformed_SD =  1.139

95th =  exp(0.504 + 1.645 * 1.139) = 10.8    > AMEL(4.1)

99th =  exp(0.504 + 2.326 * 1.139) = 23.4  > MDEL(8.2)

Infeasibility Concluded Since:

95th > AMEL therefore Infeasible to Comply

99th > MDEL therefore Infeasible to Comply

PBEL = exp(0.504 + 3 * 1.139) = 50.5

Descriptive Statistics: ESTIMATE

Variable             N       Mean     Median     TrMean      StDev    SE Mean

ESTIMATE             9      0.504      0.381      0.504      1.139      0.380

Variable       Minimum    Maximum         Q1         Q3

ESTIMATE        -1.195      2.079     -0.450      1.701

| Name | Date | Concentration (µg/L) | MDL (µg/L) | ln(Con) | ln(MDL) |
| --- | --- | --- | --- | --- | --- |
| Selenium | 03/14/02 | 2 |  | 0.693 |  |
| Selenium | 04/18/02 | 6 |  | 1.792 |  |
| Selenium | 08/12/02 | ND | 0.5 |  | -0.693 |
| Selenium | 11/20/02 | ND | 0.5 |  | -0.693 |
| Selenium | 02/04/03 | ND | 0.5 |  | -0.693 |
| Selenium | 03/05/03 | 5 |  | 1.609 |  |
| Selenium | 05/08/03 | 8 |  | 2.079 |  |
| Selenium | 06/17/03 | ND | 0.5 |  | -0.693 |
| Selenium | 07/30/03 | ND | 0.5 |  | -0.693 |

(Not enough data for symmetry plot)

(5) ZINC

-1/2 Power-Normal Distribution Best (AD=0.65; P-value=0.686)

(-1/2 power distribution fit better than log-normal distribution)

Transformed_Mean =  0.2196

Transformed_SD =  0.0794

95th =  (0.2196 - 1.645 * 0.0794)-2 = 126.3    < AMEL(388)

99th =  (0.2196 - 2.326 * 0.0794)-2  = 820.3  < MDEL(991)

Mean of untransformed data = 23.3 < LTA(195.8)

Feasibility Concluded Since:

95th < AMEL therefore Feasible to Comply

99th < MDEL therefore Feasible to Comply

Mean < LTA therefore Feasible to Comply

Descriptive Statistics: ESTIMATE

Variable             N       Mean     Median     TrMean      StDev    SE Mean

ESTIMATE            30     0.2196     0.2240     0.2216     0.0794     0.0145

Variable       Minimum    Maximum         Q1         Q3

ESTIMATE        0.0567     0.3540     0.1727     0.2725

| Name | Date | Concentration (µg/L) | MDL (µg/L) | ln(Con) | ln(MDL) | Con-1/2 | MDL-1/2 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Zinc | 06/01/00 | 12 |  | 2.485 |  | 0.289 |  |
| Zinc | 07/01/00 | 22 |  | 3.091 |  | 0.213 |  |
| Zinc | 08/01/00 | 20 |  | 2.996 |  | 0.224 |  |
| Zinc | 09/01/00 | 14 |  | 2.639 |  | 0.267 |  |
| Zinc | 10/01/00 | 15 |  | 2.708 |  | 0.258 |  |
| Zinc | 11/01/00 | 24 |  | 3.178 |  | 0.204 |  |
| Zinc | 12/01/00 | ND | 5 |  | 1.609 |  | 0.447 |
| Zinc | 01/01/01 | 9.7 |  | 2.272 |  | 0.321 |  |
| Zinc | 02/01/01 | 80 |  | 4.382 |  | 0.112 |  |
| Zinc | 03/01/01 | 24 |  | 3.178 |  | 0.204 |  |
| Zinc | 04/01/01 | 12 |  | 2.485 |  | 0.289 |  |
| Zinc | 05/01/01 | 20 |  | 2.996 |  | 0.224 |  |
| Zinc | 06/01/01 | 14 |  | 2.639 |  | 0.267 |  |
| Zinc | 07/01/01 | 44 |  | 3.784 |  | 0.151 |  |
| Zinc | 08/01/01 | ND | 5 |  | 1.609 |  | 0.447 |
| Zinc | 09/01/01 | 9.6 |  | 2.262 |  | 0.323 |  |
| Zinc | 10/01/01 | 8 |  | 2.079 |  | 0.354 |  |
| Zinc | 11/01/01 | 18 |  | 2.890 |  | 0.236 |  |
| Zinc | 12/01/01 | 20 |  | 2.996 |  | 0.224 |  |
| Zinc | 01/01/02 | 10 |  | 2.303 |  | 0.316 |  |
| Zinc | 02/01/02 | ND | 5 |  | 1.609 |  | 0.447 |
| Zinc | 03/14/02 | 25 |  | 3.219 |  | 0.200 |  |
| Zinc | 04/18/02 | 24 |  | 3.178 |  | 0.204 |  |
| Zinc | 08/12/02 | 9 |  | 2.197 |  | 0.333 |  |
| Zinc | 11/20/02 | 15 |  | 2.708 |  | 0.258 |  |
| Zinc | 02/04/03 | 52 |  | 3.951 |  | 0.139 |  |
| Zinc | 03/05/03 | 25 |  | 3.219 |  | 0.200 |  |
| Zinc | 05/08/03 | 31 |  | 3.434 |  | 0.180 |  |
| Zinc | 06/17/03 | 120 |  | 4.787 |  | 0.091 |  |
| Zinc | 07/30/03 | 14 |  | 2.639 |  | 0.267 |  |

(6) Cyanide

Log-Normal Distribution Best (AD=2.311; P-value=0.033)
  (It is unclear which distribution is best.  Assume log-normal based on symmetry plot)

Mean =  -0.088

SD =  1.889

95th =  exp(-0.088 + 1.645 * 1.889) = 20.5    > AMEL(3.2)

99th =  exp(-0.088 + 2.326 * 1.889) =  74.1   > MDEL(6.4)

Infeasibility Concluded Since:

95th > AMEL therefore Infeasible to Comply

99th > MDEL therefore Infeasible to Comply

PBEL = exp(-0.088 + 3 * 1.889) = 19.2

Descriptive Statistics: ESTIMATE

Variable             N       Mean     Median     TrMean      StDev    SE Mean

ESTIMATE            16     -0.088      0.252     -0.075      1.889      0.472

Variable       Minimum    Maximum         Q1         Q3

ESTIMATE        -2.996      2.639     -1.880      1.619

| Name | Date | Concentration (µg/L) | MDL (µg/L) | ln(Con) | ln(MDL) |
| --- | --- | --- | --- | --- | --- |
| Cyanide | 06/01/00 | ND | 10 |  | 2.303 |
| Cyanide | 07/01/00 | ND | 10 |  | 2.303 |
| Cyanide | 10/01/00 | ND | 10 |  | 2.303 |
| Cyanide | 01/01/01 | ND | 10 |  | 2.303 |
| Cyanide | 04/01/01 | ND | 10 |  | 2.303 |
| Cyanide | 06/01/01 | ND | 10 |  | 2.303 |
| Cyanide | 08/01/01 | ND | 10 |  | 2.303 |
| Cyanide | 12/01/01 | ND | 10 |  | 2.303 |
| Cyanide | 01/01/02 | 0.05 |  | -2.996 |  |
| Cyanide | 08/12/02 | 3 |  | 1.099 |  |
| Cyanide | 11/20/02 | ND | 0.9 |  | -0.105 |
| Cyanide | 02/04/03 | 9 |  | 2.197 |  |
| Cyanide | 03/05/03 | 3 |  | 1.099 |  |
| Cyanide | 05/08/03 | 14 |  | 2.639 |  |
| Cyanide | 06/17/03 | 6 |  | 1.792 |  |
| Cyanide | 07/30/03 | ND | 0.9 |  | -0.105 |

(7) Dioxin-TEQ (2,3,7,8 TCDD)

Because all dioxin and furan effluent measurements are non-detects and the detection limits are above the WQBELs, the Board cannot determine whether it is feasibile for the Discharger to immediately comply with the WQBELs.  Therefore, consistent with a 2002 court ruling, the Board concludes infeasibility.

At this time an interim limit cannot be determined for dioxin TEQ since neither a previous permit limit exists, nor is there enough information to determine  an interim limit based on current treatment facility performance.  Because the monitoring data consists of all non-detect values, the Board cannot determine an IPBL with a meaningful statistical analysis.  Nor can the IPBEL be based at levels which the Discharger can demonstrate compliance, since the SIP does not provide ML’s for Dioxin TEQ.  If a ML is agreed upon by the Board and the Discharger, and in consultation with the State Water Resource Control Board’s Quality Assuarance Program, as specified in Section 2.4.3 of the SIP, or if additional data enables Board staff to establish performance-based limits, a new interim limit for dioxin TEQ may be calculated.

(8) 4,4'-DDE,    and (9) Dieldrin

Because all 4,4’-DDE and dieldrin effluent measurements are non-detects and the detection limits are above the WQBELs, the Board cannot determine whether it is feasibile for the Discharger to immediately comply with the WQBELs.  Therefore, consistent with a 2002 court ruling, the Board concludes infeasibility.

Because the previous permit does not include a limitation for 4,4’-DDE or for dieldrin, the interim limit must be set to the IPBL.  Because the monitoring data consisted of all non-detect values, the Board cannot determine an IPBL with a meaningful statistical analysis, but must base it at levels which the Discharger can demonstrate compliance.  In accordance with compliance determination rules specified in Section 2.4.5 of the SIP, the interim limitations are therefore set at the MLs listed in Appendix 4 of the SIP as follows: 4,4’-DDE is 0.05 µg/L, and dieldrin is 0.01 µg/L.