CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN FRANCISCO BAY REGION

1515 CLAY STREET, SUITE 1400

OAKLAND, CA  94612

(510) 622 – 2300     Fax: (510) 622 - 2460

FACT SHEET

for

REISSUANCE OF

NPDES PERMIT and WASTE DISCHARGE REQUIREMENTS for

CITY OF SUNNYVALE

WATER POLLUTION CONTROL PLANT

SUNNYVALE, SANTA CLARA COUNTY

NPDES Permit No. CA0037621

ORDER NO. R2-2003-XXXX

PUBLIC NOTICE:

# Written Comments

- Interested persons are invited to submit written comments concerning this draft permit.

- Comments must be submitted to the Regional Board no later than 5:00 p.m. on August 1, 2003.

- Send comments to the Attention of Linda Rao.

# Public Hearing

- The draft permit will be considered for adoption by the Board at a public hearing during the Board’s regular monthly meeting at: Elihu Harris State Office Building, 1515 Clay Street, Oakland, CA; 1st floor Auditorium.

- This meeting will be held on:		August 20, 2003, starting at 9:00 am.

# Additional Information

- For additional information about this matter, interested persons should contact Regional Board staff member:	Ms. Linda Rao, email: lcr@rb2.swrcb.ca.gov, Phone: (510) 622-2445;

This Fact Sheet contains information regarding an amendment of waste discharge requirements and National Pollutant Discharge Elimination System (NPDES) permit for the City of Sunnyvale municipal wastewater discharges.  The Fact Sheet describes the factual, legal, and methodological basis for the sections addressed in the Tentative Order and provides supporting documentation to explain the rationale and assumptions used in revising the effluent limitations.

I.	INTRODUCTION

The Discharger applied to the Board for reissuance of waste discharge requirements and a permit to discharge municipal wastewater to waters of the State and the United States under the NPDES.  The application and Report of Waste Discharge is dated December 14, 2002.

The Discharger owns and operates the Sunnyvale Water Pollution Control Plant (the Plant), located at 1444 Borregas Avenue, Sunnyvale, California.  The Plant treatment process consists of influent grinding, preaeration/grit removal, primary sedimentation, secondary biological treatment (oxidation ponds), fixed-film reactor nitrification, dissolved air flotation with coagulation, dual media filtration, chlorination, and dechlorination.  From 1999-2001, the average dry weather effluent flow (ADWF) was approximately 12.7 million gallons per day (MGD).  This value represents the net plant effluent, excluding recycled water flows.  Recycled water flows over the same period averaged approximately 0.36 MGD.  The treatment plant has an average dry weather flow design capacity of approximately 29.5 MGD.  The USEPA and the Board have classified this Discharger as a major discharger.  The receiving waters for the subject discharges are the waters of Moffett Channel, tributary to Guadalupe Slough and South San Francisco Bay.  The beneficial uses for South San Francisco Bay, as identified in the Basin Plan and based on known uses of the receiving waters near the discharge, are:

- Industrial Service Supply

- Navigation

- Water Contact Recreation

- Non-contact Water Recreation

- Commercial and Sport Fishing

- Wildlife Habitat

- Preservation of Rare and Endangered Species

- Fish Migration

- Fish Spawning (potential for San Francisco Bay)

- Estuarine Habitat

- Shellfish Harvesting

Beneficial uses specific to Moffett Channel and Guadeloupe Slough have not been assessed to determine which uses exist or potentially could exist.  Board policy is to use the tributary rule to interpret which beneficial uses are currently or potentially supported where beneficial uses have not been specifically designated.  The beneficial uses of South San Francisco Bay, therefore, are assumed to apply to the Moffett Channel and Guadeloupe Slough.

While South San Francisco Bay is generally marine in character, both the Moffett Channel and the Guadeloupe Slough are estuarine in character and tidally influenced.  Therefore, the reasonable potential analysis and effluent limitations specified in this Order are based on lower of the salt and freshwater California Toxics Rule (CTR) and National Toxics Rule (NTR) water quality criteria (WQC).

II.	DESCRIPTION OF EFFLUENT

The table below presents the quality of the discharge, as indicated in the Discharger’s self-monitoring reports submitted for the period from January 1999 through March 2002.  Average values represent the average of actual detected values only.

Table A.  Summary of Discharge Data

| Parameter | Average | Daily Maximum |
| --- | --- | --- |
| CBOD (mg/L) | 4.63 | 53.7 |
| CBOD Removal (%) | 96.8 | 93.6 (min monthly) |
| TSS (mg/L)* | 7.93 | 20.1 |
| TSS Removal (%) | 93.6 | 90.0 (min monthly) |
| Total Organic Carbon (mg/L) | 13.931 | 25.3 |
| Oil and Grease (mg/L) | 1.53 | 2.15 |
| Total Settleable Solids (ml/l-hr)* | 0.0 | 0.0 |
| Residual Chlorine* | 1.2 (1 detected value) 2 | 1.2 |
| Turbidity (NTU)* | 6.5 | 10.5 |
| pH (standard units)* | 6 (min.) | 8.3 |
| Ammonia (as N) | 3.6 | 15 |
| Nitrite (mg/L) | 0.35 | 1.37 |
| Nitrate (mg/L) | 13.07 | 45.5 |
| Organic-N (mg/L) | 3.56 | 15.2 |
| Phosphorous (mg/L) | 6.73 | 16.6 |
| Dissolved Oxygen (mg/L) | 7.43 | 2.3 (min.) |
| Total Coliform (mpn/100 ml)* | --3 | 2400 |
| Arsenic (g/L) | 1.6 | 7.0 |
| Total Chromium (g/L) | 0.8 | 1.8 |
| Chromium (VI) (g/L) | 2.81 | 7 |
| Copper (g/L)* | 2.4 | 6.2 |
| Lead (g/L) | 1.4 | 1.8 |
| Mercury (g/L)* | 0.004 | 0.012 |
| Nickel (g/L)* | 2.7 | 4.6 |
| Selenium (g/L) | 1.3 | 2.7 |
| Silver (ug/L) | 0.3 | 1.0 |
| Zinc (g/L) | 26.7 | 110 |
| Cyanide* | 8.4 | 29.0 |
| Bromoform | 5.87 | 14.0 |
| Chlordibromomethane (g/L) | 19.5 | 40 |
| Chloroform (g/L) | 10.4 | 34 |
| Dichlorobromomethane (g/L) | 20.1 | 46 |
| Methyl Bromide | 11 | 28 |
| Methyl Chloride | 1.04 | 1.0 |
| Tetrachloroethylene | 54 | 5 |
| Toluene | 14 | 1 |
| 1,2-Trans-Dichloroethylene | 14 | 1 |
| Trichloroethylene | 24 | 2 |
| Phenol | 3.0 | 6 |
| Endrin** | 0.024 | 0.02 |
| Tributyltin (g/L)* | 0.03 | 0.19 |

* Current permit contains effluent concentration limitations for these constituents.

** Current permit contains effluent concentration goals for these constituents.

1 These data are from January 2000 through March 2002.

2	These data are for 1999 only.

3 Only 30 of 1,079 samples were detectable. The maximum value was 2400 MPN/100 ml and the other detectable values ranged from 2 MPN/100 ml to 240 MPN/100 ml. All other values were <2 MPN/100 ml.

4 Only one detected value, therefore the average value is also the maximum value.

III.	GENERAL RATIONALE

The following documents are the bases for the requirements contained in the proposed Order, and are referred to under the specific rationale section of this Fact Sheet.

- Federal Water Pollution Control Act, as amended (hereinafter the CWA).

- Federal Code of Regulations, Title 40 - Protection of Environment, Chapter 1, Environmental Protection Agency, Subchapter D, Water Programs, Parts 122-129 (hereinafter referred to as 40 CFR specific part number).

- Water Quality Control Plan, San Francisco Bay Basin, adopted by the Board on June 21, 1995 (hereinafter the Basin Plan).  The California State Water Resources Control Board (hereinafter the State Board) approved the Basin Plan on July 20, 1995 and by California State Office of Administrative Law approved it on November 13, 1995.  The Basin Plan defines beneficial uses and contains WQOs for most waters of the State.  However, the numeric WQOs for priority pollutants in the Basin Plan do not apply to the South Bay below Dumbarton Bridge.  On May 22, 2002, the Board adopted a Basin Plan Amendment that includes site-specific objectives (SSOs) for copper and nickel that apply to the South Bay.

- California Toxics Rules, Federal Register, Vol. 65, No. 97, May 18, 2000 (hereinafter the CTR).

- National Toxics Rules 57 FR 60848, December 22, 1992, as amended (hereinafter the NTR).

- State Board’s Policy for Implementation of Toxics Standards for Inland Surface Waters, Enclosed Bays, and Estuaries of California, May 1, 2000 (hereinafter the State Implementation Policy, or SIP).

- Ambient Water Quality Criteria for Bacteria – 1986, USEPA 440/5-84-002, January 1986.

- USEPA Technical Support Document for Water Quality-Based Toxics Control, EPA/505/2-90-001, March 1991 (hereinafter TSD).

IV.	SPECIFIC RATIONALE

Several specific factors affecting the development of limitations and requirements in the proposed Order are discussed as follows:

1.	Recent Plant Performance

Section 402(o) of CWA and 40 CFR § 122.44(l) require that water quality-based effluent limitations (WQBELs) in re-issued permits be at least as stringent as in the previous permit.  The SIP specifies that interim effluent limitations, if required, must be based on current treatment facility performance or on existing permit limitations whichever is more stringent (unless anti-backsliding requirements are met).  In determining what constitutes “recent plant performance”, best professional judgment (BPJ) was used.  Effluent monitoring data collected from 1999 to 2002 are considered representative of recent plant performance.

2.	Impaired Water Bodies in 303(d) List

On June 6, 2003, the USEPA approved a revised list of impaired waterbodies prepared by the State.  The list (hereinafter referred to as the 2003 303(d) list was prepared in accordance with Section 303(d) of the federal Clean Water Act to identify specific water bodies where water quality standards are not expected to be met after implementation of technology-based effluent limitations on point sources.  South San Francisco Bay is listed as an impaired waterbody. The pollutants impairing South San Francisco Bay include chlordane, DDT, diazinon, dieldrin, dioxin compounds, exotic species, furan compounds, mercury, PCBs, dioxin-like PCBs, and selenium.  Copper and nickel, which were previously identified as impairing South San Francisco Bay, were not included as impairing pollutants in the 2003 303(d) list and have been placed on the new Monitoring List.

The SIP requires final effluent limitations for all 303(d)-listed pollutants to be based on total maximum daily loads (TMDLs) and wasteload allocation (WLA) results.  The SIP and federal regulations also require that final concentration limitations be included for all pollutants with reasonable potential.  The SIP requires that where the Discharger has demonstrated infeasibility to meet the final limitations, interim concentration limitations be established in the permit with a compliance schedule in effect until final effluent limitations are adopted.  The SIP also requires the inclusion of appropriate provisions for waste minimization and source control.

3.	Basis for Prohibitions

- Prohibition A.1 (no discharges other than as described in the permit): This prohibition is based on the Basin Plan, previous Order, and BPJ.

- Prohibitions A.2 (10:1 dilution), A.3 (dead-end sloughs/confined waterbodies), and A.4 (no discharge to South San Francisco below Dumbarton Bridge or its tributaries): These prohibitions are based on the Basin Plan.

- Prohibition A.5 (no bypass or overflow): This prohibition is based on the previous Order and BPJ.

- Prohibition A.6 (no unauthorized discharge): This prohibition is based on the Basin Plan, the and the Clean Water Act, which prohibit unauthorized/unpermitted discharges.

- Prohibition A.7 (flow limitation):  This prohibition is based on the reliable treatment capacity of the plant. Exceedence of the treatment plant's average dry weather flow design capacity may result in lowering the reliability of compliance with water quality requirements, unless the Discharger demonstrates otherwise through an antidegradation study. This prohibition is based on 40 CFR 122.41(l).

- Prohibition A.8 (discharge prohibition exception):  As discussed in detail in the Order, the Board has continued the Discharger’s exception from Prohibitions A.2-A.4 based on an equivalent level of environmental protection.

4.	Basis for Effluent Limitations

- Effluent Limitation B.1:  These limitations are technology-based and other limitations representative of, and intended to ensure, adequate and reliable advanced secondary level wastewater treatment.  They are at least as stringent as the Basin Plan requirements (Chapter 4, pg 4-8, and Table 4-2, at pg 4-69).  The limitations are unchanged from the previous permit. Compliance has been demonstrated by existing plant performance.

Provision E.9 of the previous Order required the Discharge to complete a study on the effects of ammonia in the discharge on the receiving water and the appropriate effluent limitations.  In part, this study was required because of reduced ammonia removal at the plant during winter months and occasional occurrence of low dissolved oxygen levels in the receiving water.   On June 29, 2001, the Discharger submitted to the Board - City of Sunnyvale Receiving Water Ammonia Investigations Final Report.  This report indicates that unionized ammonia levels in the discharge do not cause toxicity in the receiving water and total ammonia in the effluent likely does not contribute to the seasonally depressed dissolved oxygen levels.  Based on these findings, the Board has retained the existing permit limitations for ammonia, i.e., numeric limitations that only apply during June through September.

- Effluent Limitation B.2 (pH):  This effluent limitation is unchanged from the existing permit. The limitation is based on the Basin Plan (Chapter 4, Table 4-2), which is derived from federal requirements (40 CFR 133.102).  This is an existing permit effluent limitation and compliance has been demonstrated by existing plant performance.  The Discharger may elect to use continuous on-line monitoring system(s) for measuring pH.  In this case, 40 CFR 401.17 (pH Effluent Limitations Under Continuous Monitoring) and BPJ are the basis for the compliance provisions for pH limitations.  Excursions outside of the pH effluent limitations are permitted, provided that both of the following conditions are satisfied:

- The total time during which the pH values are outside the required range of pH values shall not exceed 7 hours and 26 minutes in any calendar month; and

- No individual excursion from the range of pH values shall exceed 60 minutes.

- Effluent Limitation B.3 (CBOD and TSS monthly average 85 percent removal): These are standard secondary treatment requirements and existing permit effluent limitations based on Basin Plan requirements (Table 4-2, pg. 4–69), derived from federal requirements (40 CFR 133.102; definition in 133.101).  Compliance has been demonstrated by existing plant performance for ordinary flows (dry weather flows and most wet weather flows). During the past few years, the Discharger has consistently met these removal efficiency limitations.

- Effluent Limitation B.4 (Whole Effluent Acute Toxicity):  The Basin Plan specifies a narrative objective for toxicity, requiring that all waters shall be maintained free of toxic substances in concentrations that are lethal to or produce other detrimental response on aquatic organisms.  Detrimental response includes but is not limited to decreased growth rate, decreased reproductive success of resident or indicator species, and/or significant alternations in population, community ecology, or receiving water biota.  These effluent toxicity limitations are necessary to ensure that this objective is protected.  The whole effluent acute toxicity limitations for a eleven-sample median and single sample maximum are consistent with the previous Order and are based on the Basin Plan (Table 4-4, pg. 4–70).  The limitations remain unchanged in this Order.  During 1999-2001, the eleven sample median survival was 100 percent.  The 90th percentile survival was between 96-100 percent.

- Effluent Limitation B.5 (Whole Effluent Chronic Toxicity):  The chronic toxicity objective/limitation is based on the Basin Plan’s narrative toxicity objective on page 3-4.

- Effluent Limitations B.6 and B.7 (Toxic Substances):

  - Reasonable Potential Analysis (RPA):

40 CFR 122.44(d)(1)(i) specifies that permits are required to include WQBELs for all pollutants “which the Director determines are or may be discharged at a level which will cause, have the reasonable potential to cause, or contribute to an excursion above any State water quality standard”.  Thus, the fundamental step in determining whether or not a WQBEL is required is to assess a pollutant’s reasonable potential of excursion of its applicable WQO or WQC.  The following section describes the reasonable potential analysis and the results of such an analysis for the pollutants identified in the Basin Plan and the CTR.

    - SSOs and WQC:  The RPA involves the comparison of effluent data with appropriate SSOs for copper and nickel adopted in the Basin Plan Amendment (adopted by the Board on May 22, 2002 and the approved by the State Board on October 17, 2002), applicable WQC in the CTR/NTR, and USEPA’s 1986 Quality Criteria for Water.  The SSOs and CTR criteria are shown in Attachment 1 of this Fact Sheet.

- In the May 22, 2002 Basin Plan Amendments, the Board also adopted metals translators specific to Lower South San Francisco Bay for copper and nickel.  The translators for copper and nickel are 0.53 and 0.44, respectively.  The translator development rationale and approach are discussed in the Staff Report to the May 22, 2002 SSO Basin Plan Amendments.

    - Methodology:  The RPA is conducted using the method and procedures prescribed in Section 1.3 of the SIP.  Board staff has analyzed the effluent and background data and the nature of facility operations to determine if the discharge has reasonable potential to cause or contribute to exceedances of applicable SSOs or WQC.  Attachment 1 of this Fact Sheet shows the step-wise process described in Section 1.3 of the SIP.

    - Effluent and background data:  The receiving waters for the discharges are estuarine and subject to complex tidal conditions of the Lower South San Francisco Bay.  Therefore, the most representative location of ambient background data in the Lower South San Francisco Bay for this facility is the Dumbarton Bridge RMP station (B-A-30).  The RPA was completed using RMP data from 1993 through 2000 for the Dumbarton RMP.

    - RPA determination: The RPA results are shown below in Table B and Attachment 1 of this Fact Sheet.  The pollutants that exhibit RP are copper, nickel, mercury, cyanide, chlorodibromomethane, dichlorobromomethane, endrin, 4,4’-DDE, dieldrin, indeno(1,2,3-cd)pyrene, benzo(b)fluoranthene, heptachlor epoxide, tributyltin, and 2,3,7,8-TCDD.

#### Table B.  Summary of Reasonable Potential Results

| - # in CTR | - PRIORITY POLLUTANTS | - MEC or Minimum DL1 - (g/L) | - Governing WQO/WQC (ug/L) | - Maximum Background - (g/L) | - RPA Results2 |
| --- | --- | --- | --- | --- | --- |
| - 2 | - Arsenic | 3.1 | 36 | 4.59 | N |
| - 4 | - Cadmium | 0.2 | 2.52 | 0.1707 | N |
| - 5b | - Chromium (VI) | NA | 200 | 14.74 | N3 |
| - 6 | - Copper | 6.2 | 13.02 | 7.19 | Y4 |
| - 7 | - Lead | 1.8 | 52 | 3.78 | N3 |
| - 8 | ###### Mercury | 0.009 | 0.051 | 0.0682 | Y |
| - 9 | - Nickel | 4.6 | 27.05 | 13.03 | Y4 |
| - 10 | - Selenium | 2.7 | 5 | 0.63 | N |
| - 11 | ###### Silver | 1 | 2.24 | 0.1193 | N |
| - 13 | - Zinc | 110 | 122.86 | 14.85 | N3 |
| - 14 | ###### Cyanide | 29 | 1 | NA | Y |
| - 16 | - 2,3,7,8-TCDD (Dioxin) | 1.6 | 1.4E-08 | NA | Y5 |
| - 17 | - Acrolein | 5 | 780 | NA | N |
| - 18 | - Acrylonitrile | 2 | 0.66 | NA | N |
| - 19 | - Benzene | 0.5 | 71 | NA | N |
| - 20 | ###### Bromoform | 14 | 360 | NA | N |
| - 21 | - Carbon Tetrachloride | 0.5 | 4.4 | NA | N |
| - 22 | - Chlorobenzene | 0.5 | 21000 | NA | N |
| - 23 | - Chlorodibromomethane | 40 | 34 | NA | Y |
| - 24 | - Chloroethane | 0.5 | NA | NA | Uo |
| - 25 | - 2-Chloroethylvinyl Ether | 1 | NA | NA | Uo |
| - 26 | - Chloroform | 34 | NA | NA | Uo |
| - 27 | - Dichlorobromomethane | 46 | 46 | NA | Y |
| - 28 | - 1,1-Dichloroethane | 0.5 | NA | NA | Uo |
| - 29 | - 1,2-Dichloroethane | 0.5 | 99 | NA | N |
| - 30 | - 1,1-Dichloroethylene | 0.5 | 3.2 | NA | N |
| - 31 | - 1,2-Dichloropropane | 0.5 | 39 | NA | N |
| - 32 | - 1,3-Dichloropropylene | 0.5 | 1700 | NA | N |
| - 33 | - Ethylbenzene | 0.5 | 29000 | NA | N |
| - 34 | - Methyl Bromide | 28 | 4000 | NA | N |
| - 35 | - Methyl Chloride | 1 | NA | NA | Uo |
| - 36 | - Methylene Chloride | 1 | 1600 | NA | N |
| - 37 | - 1,1,2,2-Tetrachloroethane | 0.5 | 11 | NA | N |
| - 38 | - Tetrachloroethylene | 5 | 8.85 | NA | N |
| - 39 | - Toluene | 1 | 200000 | NA | N |
| - 40 | - 1,2-Trans-Dichloroethylene | 1 | 140000 | NA | N |
| - 41 | - 1,1,1-Trichloroethane | 0.5 | NA | NA | Uo |
| - 42 | - 1,1,2-Trichloroethane | 0.5 | 42 | NA | N |
| - 43 | - Trichloroethylene | 2 | 81 | NA | N |
| - 44 | - Vinyl Chloride | 0.5 | 525 | NA | N |
| - 45 | - Chlorophenol | 2 | 400 | NA | N |
| - 46 | - 2,4-Dichlorophenol | 1 | 790 | NA | N |
| - 47 | - 2,4-Dimethylphenol | 2 | 2300 | NA | N |
| - 48 | - 2-Methyl-4,6-Dinitrophenol | 5 | 765 | NA | N |
| - 49 | - 2,4-Dinitrophenol | 5 | 14000 | NA | N |
| - 50 | - 2-Nitrophenol | 2 | NA | NA | Uo |
| - 51 | - 4-Nitrophenol | 5 | NA | NA | Uo |
| - 52 | - 3-Methyl-4-Chlorophenol | 1 | NA | NA | Uo |
| - 53 | - Pentachlorophenol | 1 | 7.9 | NA | N |
| - 54 | - Phenol | 6 | 500 | NA | N |
| - 55 | - 2,4,6-Trichlorophenol | 5 | 6.5 | NA | N |
| - 56 | - Acenaphthene | 0.3 | 2700 | 0.0026 | N |
| - 57 | - Acenaphthylene | 0.2 | NA | 0.00054 | Uo |
| - 58 | - Anthracene | 0.1 | 110000 | 0.0023 | N |
| - 59 | - Benzidine | 5 | 0.00054 | NA | N |
| - 60 | - Benzo(a)Anthracene | 0.2 | 0.049 | 0.017 | N |
| - 61 | - Benzo(a)Pyrene | 0.2 | 0.049 | 0.045 | N |
| - 62 | - Benzo(b)Fluoranthene | 0.2 | 0.049 | 0.0572 | Y |
| - 63 | - Benzo(ghi)Perylene | 0.3 | NA | 0.015 | Uo |
| - 64 | - Benzo(k)Fluoranthene | 0.2 | 0.049 | 0.02105 | N |
| - 65 | - Bis(2-Chloroethoxy)Methane | 2 | NA | NA | Uo |
| - 66 | - Bis(2-Chloroethyl)Ether | 1 | 1.4 | NA | N |
| - 67 | - Bis(2-Chloroisopropyl)Ether | 2 | 170000 | NA | N |
| - 68 | - Bis(2-Ethylhexyl)Phthalate | 5 | 5.9 | NA | N |
| - 69 | - 4-Bromophenyl Phenyl Ether | 2 | NA | NA | Uo |
| - 70 | - Butylbenzyl Phthalate | 2 | 5200 | NA | N |
| - 71 | - 2-Chloronaphthalene | 2 | 4300 | NA | N |
| - 72 | - 4-Chlorophenyl Phenyl Ether | 2 | NA | NA | Uo |
| - 73 | - Chrysene | 0.3 | 0.049 | 0.02206 | N |
| - 74 | - Dibenzo(a,h)Anthracene | 0.1 | 0.049 | 0.0088 | N |
| - 75 | - 1,2 Dichlorobenzene | 0.5 | 17000 | NA | N |
| - 76 | - 1,3 Dichlorobenzene | 0.5 | 2600 | NA | N |
| - 77 | - 1,4 Dichlorobenzene | 0.5 | 2600 | NA | N |
| - 78 | - 3,3-Dichlorobenzidine | 5 | 0.077 | NA | N |
| - 79 | - Diethyl Phthalate | 2 | 120000 | NA | N |
| - 80 | - Dimethyl Phthalate | 2 | 2900000 | NA | N |
| - 81 | - Di-n-Butyl Phthalate | 2 | 12000 | NA | N |
| - 82 | - 2,4-Dinitrotoluene | 2 | 9.1 | NA | N |
| - 83 | - 2,6-Dinitrotoluene | 2 | NA | NA | Uo |
| - 84 | - Di-n-Octyl Phthalate | 2 | NA | NA | Uo |
| - 85 | - 1,2-Diphenylhydrazine | 1 | 0.54 | NA | N |
| - 86 | - Fluoranthene | 0.05 | 370 | 0.03896 | N |
| - 87 | - Fluorene | 0.1 | 14000 | 0.0055 | N |
| - 88 | - Hexachlorobenzene | 1 | 0.00077 | 0.000164 | N |
| - 89 | - Hexachlorobutadiene | 1 | 50 | NA | N |
| - 90 | - Hexachlorocyclopentadiene | 2 | 17000 | NA | N |
| - 91 | - Hexachloroethane | 1 | 8.9 | NA | N |
| - 92 | ###### Indeno(1,2,3-cd) Pyrene | 0.05 | 0.049 | 0.078 | Y |
| - 93 | - Isophorone | 1 | 600 | NA | N |
| - 94 | - Naphthalene | 0.2 | NA | 0.0024 | Uo |
| - 95 | - Nitrobenzene | 1 | 1900 | NA | N |
| - 96 | - N-Nitrosodimethylamine | 2 | 8.1 | NA | Ud |
| - 97 | - N-Nitrosodi-n-Propylamine | 2 | 1.4 | NA | N |
| - 98 | - N-Nitrosodiphenylamine | 1 | 16 | NA | N |
| - 99 | - Phenanthrene | 0.05 | NA | 0.0141 | Uo |
| - 100 | - Pyrene | 0.05 | 11000 | 0.05603 | N |
| - 101 | - 1,2,4-Trichlorobenzene | 0.6 | NA | NA | Uo |
| - 102 | - Aldrin | 0.005 | 0.00014 | NA | N |
| - 103 | - alpha-BHC | 0.01 | 0.013 | 0.000662 | N |
| - 104 | - beta-BHC | 0.005 | 0.046 | 0.000607 | N |
| - 105 | - gamma-BHC | 0.01 | 0.063 | 0.0016667 | N |
| - 106 | - delta-BHC | 0.005 | NA | 0.000133 | Uo |
| - 107 | - Chlordane | 0.01 | 0.00059 | 0.000574 | N |
| - 108 | - 4,4’-DDT | 0.01 | 0.00059 | 0.000202 | N |
| - 109 | - 4,4’-DDE | 0.01 | 0.00059 | 0.000678 | Y |
| - 110 | - 4,4’-DDD | 0.01 | 0.00084 | 0.00077 | N |
| - 111 | - Dieldrin | 0.01 | 0.00014 | 0.000292 | Y |
| - 112 | - alpha-Endosulfan | 0.01 | 0.0087 | 0.000027 | N |
| - 113 | - beta-Endosulfan | 0.01 | 0.0087 | 0.000046 | N |
| - 114 | - Endosulfan Sulfate | 0.01 | 240 | 0.000072 | N |
| - 115 | - Endrin | 0.02 | 0.0023 | 0.00012 | Y |
| - 116 | - Endrin Aldehyde | 0.01 | 0.81 | NA | N |
| - 117 | - Heptachlor | 0.01 | 0.00021 | 0.000022 | N |
| - 118 | - Heptachlor Epoxide | 0.01 | 0.00011 | 0.000174 | Y |
| - 119-125 | - PCBs | 0.1 | 0.00017 | NA | N |
| - 126 | - Toxaphene | 0.01 | 0.0002 | NA | N |
|  | - Tributyltin | 0.19 | 0.01 | NA | Y |

- 1)	Maximum Effluent Concentration (MEC) in bold is the actual detected MEC, otherwise the MEC shown is the minimum detection level.

- NA = Not Available (there is not monitoring data for this constituent).

- 2)	RP =Yes, if (1) either MEC or Background > WQO/WQC.

- RP = No, if both MEC or background < WQO/WQC or (2) all effluent concentrations non-detect and background <WQO/WQC or no background available.

- RP = Ud (undetermined due to lack of effluent monitoring data).

- RP = Uo (undetermined if no objective promulgated).

- 3)	For all metals except copper and nickel-which utilize translators adopted in the May 22, 2002 Basin Plan Amendment, Board staff initially assessed reasonable potential using the conversion factors (Cfs)/translators included in the CTR. After this initial assessment, reasonable potential was suggested for chromium VI, lead, and zinc. Board staff have determined that the RMP data are representative of season and spatial variability in water body conditions; were collected and evaluated according to rigorous quality assurance and control requirements; and meet USEPA’s recommended guidelines for translator development.  Based on these conclusions, Board staff followed the procedures in Section 1.4.1 of the SIP to establish chromium VI, lead, and zinc translators.    Complete documentation of the data and methodology used to determine the chromium VI, lead, and zinc translators is provided in Attachment 3 to this Fact Sheet.

- 4)	RP =Yes, based on third trigger, see the Order for detailed basis for this determination for copper and nickel.

5)	RP =Yes, based on the third trigger.   Although additional, reliable ambient and effluent data are required, the San Francisco Bay Ambient Water Monitoring Interim Report provides monitoring results from sampling events in 2002 and 2003 for the Dumbarton Bridge RMP station.  While these “interim” data have not been used to evaluate RP using trigger 2, they show elevated dioxin levels at the Dumbarton Bridge RMP station.  The Board has considered these data along with the listing on the 303(d) list to find RP for dioxin based on the third trigger.

    - Constituents with limited data:  Reasonable potential could not be determined for some of the organic priority pollutants due to (i) the absence of effluent data or (ii) the absence of applicable WQC.  As required by the August 6, 2001 letter from Board staff to all permittees, the Discharger is required to initiate or continue to monitor for those pollutants in this category using analytical methods that provide the best detection limits reasonably feasible.  These pollutants’ RP will be reevaluated in the future to determine whether there is a need to add numeric effluent limitations to the permit or to continue monitoring.

    - Pollutants with no reasonable potential:  WQBELs are not included in the Order for constituents that do not have reasonable potential to cause or contribute to exceedance of applicable WQOs or WQC.  However, monitoring for those pollutants is still required, under the provisions of the August 6, 2001 letter.  If concentrations of these constituents are found to have increased significantly, the Discharger will be required to investigate the source(s) of the increase(s).  Remedial measures are required if the increases pose a threat to water quality in the receiving water.

    - Permit reopener:  The permit includes a reopener provision to allow numeric effluent limitations to be added for any constituent that in the future exhibits reasonable potential to cause or contribute to exceedance of a WQO or WQC.  This determination, based on monitoring results, will be made by the Board.

  - Final Water Quality-Based Effluent Limitations:  The final WQBELs were developed for the toxic and priority pollutants that were determined to have reasonable potential to cause or contribute to exceedances of the SSOs or WQC.  Final effluent limitations were calculated based on appropriate SSOs/WQC and the appropriate procedures specified in Section 1.4 of the SIP (See Attachment 2 of this Fact Sheet).  For the purpose of the Proposed Order, final WQBELs refer to all non-interim effluent limitations.  The SSO or WQC used for each pollutant with reasonable potential is indicated in Table C below as well as in Attachment 2.

#### Table C. Water Quality Objectives/Criteria for Pollutants with RP

| - Pollutant | - Chronic WQC (μg/L) | - Acute WQC (μg/L) | - Human Health - WQC - (μg/L) | - Basis of Lowest SSO/WQC - Used in RP |
| --- | --- | --- | --- | --- |
| - Copper | - 13.02 | - 20.38 |  | - SSO |
| - Mercury | - -- | - -- | - 0.051 | - CTR |
| - Nickel | - 27.05 | - 141.82 |  | - SSO |
| - Cyanide | - 1 | - 1 |  | NTR |
| - Chlorodibromomethane | - -- | - -- | 34 | CTR |
| - Dichlorobromomethane | - -- | - -- | 46 | CTR |
| - Benzo(b)fluoranthene | - -- | - -- | 0.049 | CTR |
| - Indeno(1,2,3-cd)pyrene | - -- | - -- | 0.049 | CTR |
| - Endrin | - 0.0023 | - 0.037 | 0.81 | CTR |
| - 4,4’-DDE | - -- | - -- | 0.00059 | CTR |
| - Dieldrin | - 0.056 | - 0.24 | 0.00014 | CTR |
| - Heptachlor Epoxide | - -- | - -- | 0.00011 | CTR |
| - Tributyltin | - 0.01 | - 0.37 | -- | USEPA Guidance |
| - TCDD TEQ | - -- | - -- | 1.4E-08 | CTR |

  - Feasibility Evaluation and Compliance Schedules: The Discharger submitted an infeasibility to comply report on March 5, 2003 for cyanide, chlorodibromomethane, dichlorobromomethane, and endrin.  For constituents for which a meaningful statistical analysis (i.e., cyanide) could be performed, the Board used self-monitoring data from 1999-2002 to compare the mean, 95th percentile, and 99th percentile with the long-term average (LTA), AMEL, and MDEL to confirm if it is feasible for the Discharger to comply with WQBELs.  If the LTA, AMEL, and MDEL all exceed the mean, 95th percentile, and 99th percentile, it is feasible for the Discharger to comply with WQBELs.  The table D below shows these comparisons in g/L:

#### Table D:  Summary of Feasibility Analysis

| Constituent | - Mean / LTA | - 95th / AMEL | - 99th / MDEL | - Feasible to Comply |
| --- | --- | --- | --- | --- |
| - Cyanide | - 9.6 > 0.4 | - 21.5 > 0.6 | - 22.2 > 1 | - No |

- For endrin, chlorodibromomethane and dichlorobromomethane, there were insufficient data to perform a meaningful statistical analysis.  Board staff, therefore, considered the 1999-2002 monitoring data for these constituents and used best professional judgment to verify that the Discharger cannot achieve immediate compliance with the final limitations.

This permit establishes compliance schedules until October 31, 2008 for cyanide, chlorodibromomethane, dichlorobromomethane, benzo(b)fluoranthene, indeno(1,2,3-cd)pyrene, 4,4’-DDE, dieldrin, and heptachlor epoxide.  As indicated in Section 2.1 of the SIP, 5 years is the maximum allowable compliance schedule duration for pollutant with final limitations derived from CTR/NTR WQC. The compliance schedules exceed the length of the permit; therefore, the calculated final limitations are intended for point of reference for the feasibility demonstration.

For dioxin, it is not feasible to determine compliance or develop an interim limit because there are insufficient reliable, low-level monitoring data.  This permit requires additional dioxin monitoring and a study to evaluate and implement analytical methods with lower detection limits.

- During the compliance schedules, interim limitations are included based on current treatment facility performance or on existing permit limitations, whichever is more stringent to maintain existing water quality.  The Board may take appropriate enforcement actions if interim limitations and requirements are not met.

  - Interim Limitations: Interim performance-based effluent concentration limitations were derived for cyanide, chlorodibromomethane, and dichlorobromomethane for which the Discharger has shown infeasibility of complying with the respective final limitations and has demonstrated that compliance schedules are justified based on the Discharger’s source control and pollution minimization efforts in the past and continued efforts in the present and future.  For endrin, there are insufficient data to determine an interim limitation and additional data collection is required by this Order.  Interim concentration and dry weather mass effluent limitations were derived for mercury pending completion of the mercury TMDL for South San Francisco Bay.  For benzo(b)fluoranthene, indeno(1,2,3-cd)pyrene, 4,4’-DDE, dieldrin, and heptachlor epoxide, compliance with the final WQBELs cannot be determined at this time as the MLs are higher than the final calculated WQBELs.  Interim limitations, therefore, are established at the respective MLs.  The interim limitations are also discussed in more detail below.

- Mercury – Further Discussion and Rationale for Interim Effluent Limitation:  Based on background data, there is reasonable potential for exceedances of the WQC for mercury.  WQBELs, therefore, are required.  Pending completion of a TMDL, this Order establishes interim effluent limitations of 12 ng/L as a monthly average limitation and 2.1 μg/L as a daily maximum limitation, which are the existing permit limitations.  Since mercury is monitored monthly, these limitations are more stringent than the statistically calculated performance-based limitation of 23 ng/L that the Board staff determined from pooled ultra-clean mercury data for POTWs throughout the Region using advanced secondary treatment (Staff Report:  Statistical Analysis of Pooled Data from Region-wide Ultra-clean Sampling, 2000).  These limitations are also more stringent than the final WQBELs (AMEL of 0.051 μg/L and MDEL of 0.093 μg/L) calculated according to the SIP methodology.

In other Orders, the Board has established interim mercury mass-based effluent limitations based on actual treatment plant performance to maintain current loadings until a TMDL is established.  This Order establishes a dry weather, interim mercury mass-based effluent limitation of 0.041 kg/month.  This limitation is calculated based on the average monthly concentration-based effluent limitation (12 ng/L) and the dry weather design capacity of the treatment plant (29.5 mgd).  This interim mass limitation only applies during the dry weather season (May through October).  The Board has determined that this mass-based limitation is appropriate for this Discharger for the following reasons:  (1) recent monitoring data show very low levels of mercury in the discharge, well below the applicable WQC, (2) the interim concentration limitations, which are more stringent than the WQBELs calculated according to the SIP methodology, will ensure that mercury levels remain low in the discharge, (3) the Discharger will continue to identify and, to the extent feasible, address mercury sources under its pollution prevention program, and (4) the interim mass limitation based on the design flow will preclude any significant increases in mass loadings from the plant. Overall, the Discharger already has minimized mercury influent loadings to the treatment plant and provided for a high level of mercury removal in the treatment process.  The Board anticipates that is unlikely that the TMDL will require additional reductions in mercury loadings beyond current treatment levels.  Further, to complement the dry weather interim limitation, the South Bay dischargers have proposed to complete scientific studies designed to further the Board’s understanding of mercury fate and transport in the South Bay and identify specific sources and potential advanced control opportunities.  As part of this effort, a provision is included in this Order requiring the Discharger to complete a study of “first flush” storm water runoff and identify and evaluate options for diverting contaminated storm water to the wastewater treatment plant to reduce mercury mass loadings.  This study, along with the work of the other South Bay dischargers, is expected to yield valuable data to support completion of the TMDL and yield further reductions in mercury loadings.

- Cyanide – Further Discussion and Rationale for Interim Effluent Limitation:  An interim performance-based concentration limitation of 32 g/L was derived for cyanide using a “pooled data” approach, which was based on the performance of Bay Area POTWs with similar treatment processes (advanced secondary treatment).  Due to the large number of samples with results below detection limits, the interim limitation was computed using the “log-Probit method” for estimating interim performance-based limitations, and provides unbiased estimates of distribution parameters and percentiles.  The interim limitation was computed using the 99.87th percentile (or three standard deviations above the mean) of the pooled effluent data, resulting in a value of 32 μg/L, expressed as a daily maximum limitation.

In the effluent data set from 1999 through 2001, cyanide was detected in 16 of 102 samples with detected values ranging from 5 to 29 μg/L.  The Discharger exceeded the existing permit limitation of 7.7 μg/L six times over this time period.  Cyanide was not detected, however, in the influent to the treatment plant suggesting that it may be formed in the treatment process.  There is also evidence to suggest that, to some degree, cyanide measured in effluents may be an artifact of the analytical method used or the result of analytical interferences.  In addition, it is not known whether the form(s) of cyanide that are measured in POTW effluents exhibit toxicity in the environment.  Provision E.8 of the previous Order required the Discharger to complete a cyanide reduction study.  To fulfill this requirement, the Discharger participated in a recently (late 2002) completed 3-year $1.5 M investigation sponsored by the Water Environment Research Foundation (WERF), that described a number of possible mechanisms for cyanide formations, and shed new light on analytical issues, but found no process or operational measures that could be implemented by the Discharger to reduce observed cyanide levels in the Discharges effluent.  The Board has determined that antibacksliding does not apply to interim limitations.  Furthermore, antidegradation is satisfied because Lower San Francisco Bay is in attainment for cyanide.

- Chlorodibromomethane and Dichlorobromomethane – Further Discussion and Rationale for Interim Effluent Limitations:  This permit establishes performance-based interim limitations of 58 and 68 g/L for chlorodibromomethane and dichlorobromomethane, respectively, derived from the arithmetic mean plus three standard deviations of the 1999-2002 effluent data set for each pollutant.  The previous permit does not include limitations for either of these pollutants.

- Endrin – Further Discussion:  The limited data preclude any meaningful statistical evaluation of current treatment performance for endrin and the previous permit does not include an endrin effluent limitation.  Because of the lack of data, this Order does not establish an interim limitation for endrin and requires the Discharger to continue monitoring for this pollutant.  When additional data become available, an interim limitation will be determined, as appropriate.  In addition, the additional data will be considered to verify reasonable potential for endrin

- Benzo(b)fluoranthene, indeno(1,2,3-cd)pyrene, 4,4’-DDE, dieldrin, and heptachlor epoxide – Further Discussion and Rationale for Interim Effluent Limitations:  Interim effluent limitations are required for these pollutants because compliance with the final WQBELs cannot be determined at this time as the MLs are higher than the final calculated WQBELs as shown in Table D.  Therefore, interim limitations are established at the respective minimum levels.

#### Table E. Final WQBELs and MLs

| - Pollutant | - AMEL(μg/L) | - MDEL (μg/L) | ML(μg/L) |
| --- | --- | --- | --- |
| - Benzo(b)fluoranthene | - 0.049 | - 0.098 | 10.0 |
| - Indeno(1,2,3-cd)pyrene | - 0.049 | - 0.098 | 0.05 |
| - 4,4’-DDE | 0.00059 | 0.00118 | 0.05 |
| - Dieldrin | 0.00014 | 0.00028 | 0.01 |
| - Heptachlor Epoxide | 0.00011 | 0.00022 | 0.01 |

- Effluent Limitation B.8 (Bacteria):  The previous Order included total coliform limitations.  USEPA’s draft implementation guidance for bacteriological water quality criteria (May, 2002) recommended either enterococcus or E. coli, or both together, as superior bacteriological indicators of human health pathogenic risk as compared to total or fecal coliform.  This recommendation was based on the fact that coliforms originate from many sources, including humans, and research has shown that many of these forms are unrelated to human pathogens or risk potential.  A growing number of studies (including the Santa Monica Bay study, Haile and others, 1999) have indicated that enterococcus and/or E. coli counts are more significantly correlated with human health problems than coliform counts.  Thus, enterococcus is recognized by USEPA and others as a fairly accurate indicator of human health risk potential from water contact.

In 2000, the City of San Jose submitted a work plan for a study to develop alternative bacteriological limitations.  On March 18, 2003, the City of San Jose submitted Alternative Effluent Bacteriological Standards, Pilot Study Report to the Board.  The Discharger subsequently on April 15, 2003 submitted a technical memorandum correlating San Jose’s study results to it’s own discharge.  The Board has accepted the correlation between the study results and included the following enterococcus limitations into this Order:

      - 30-day geometric mean of less than 35 enterococcus colonies per 100mL; and,

      - No single effluent sample exceeding 276 colonies per 100mL, as verified by a follow-up sample taken within 24 hours.

Application of these limitations is contingent on the Discharger completing a recreational use/contact survey as required by Provision E.12.  The Discharger must demonstrate through this survey that the “light” contact bacteria limitations included in this Order are appropriate for the Moffett Channel and Guadeloupe Slough.  If the “light” contact recreational use is confirmed, compliance with these limitations will reduce the required level of chlorination at the Plant.

5.	Basis for Receiving Water Limitations

a)	Receiving water limitations C.1, C.2, and C.3 (conditions to be avoided): These limitations are based on the previous Order and the narrative/numerical objectives contained in Chapter 3 of the Basin Plan, page 3-2 – 3-5.

- Receiving water limitation C.4 (compliance with State Law): This requirement is in the previous permit, requires compliance with Federal and State law, and is self-explanatory.

6.	Basis for Sludge Management Practices

These requirements are based on Table 4.1 of the Basin Plan and 40 CFR 503.

7.	Basis for Self-Monitoring Requirements

The SMP includes monitoring at the outfall for conventional, non-conventional, and toxic pollutants, and acute and chronic toxicity.  To ensure plant reliability, the Discharger is required to monitor its effluent on a daily basis.  This will be accomplished through daily turbidity monitoring. Turbidity is a good performance indicator for a tertiary treatment plant.  Turbidity is typically monitored with an on-line probe.  Because the Discharger currently monitors turbidity on a daily basis, there is no incremental cost increase.  Because of this requirement, the Board has reduced the monitoring frequencies for CBOD and TSS from three times a week to weekly and the settleable matter frequency from weekly to quarterly since these parameters are not being used to assess day-to-day performance.  In addition, the Discharger has consistently been well below the effluent limitations for these parameters.   The monitoring frequency for bacteria has been increased to five times per week.  This will provide data for assessment of compliance with the new bacteria limitations, while the Discharger reduces chlorine usage at the plant. This Order requires monthly monitoring for copper, nickel, and tributyltin to demonstrate compliance with final effluent limitations.   For mercury, cyanide, chlorodibromomethane, and dichlorobromomethane, the Discharger will also perform monthly monitoring to demonstrate compliance with interim limitations.  Monthly monitoring for endrin is also required to provide sufficient data to determine an interim limitation for this pollutant. Additionally, this Order requires twice yearly monitoring for benzo(b)fluoranthene, indeno(1,2,3-cd)pyrene, dieldrin, 4,4’-DDE, and heptachlor epoxide to demonstrate compliance with final effluent limitations.  These pollutants were not detected in the effluent during 1999-2002.  For dioxins and furans, due to the need to calculate a performance-based interim limit, this Order also requires twice yearly monitoring using methods with low detection limits.  In lieu of near field discharge specific ambient monitoring, it is generally acceptable that the Discharger participate in collaborative receiving water monitoring with other dischargers under the provisions of the August 6, 2001 letter and the RMP.

8.	Basis for Provisions

- Provisions E.1. (Permit Compliance and Rescission of Previous Permit): Time of compliance is based on 40 CFR 122. The basis of this Order superceding and rescinding the previous permit Order is 40 CFR 122.46.

- Provision E.2 (Avian Botulism Control Program):  Consistent with the specific requirements of Order WQ 90-5, compliance with this provision is a condition of the Board continuing to allow the exception from Discharge Prohibitions A.2-A.4.

- Provisions E.3 and E.4 (Chlorodibromomethane, Dichlorobromomethane, and Cyanide Compliance Schedules):  This provision is required as the Discharger cannot currently comply with final WQBELs for chlorodibromomethane, dichlorobromomethane, and cyanide.  SIP 2.2.1 requires the establishment of interim requirements and dates for their achievement in the permit.  The requirement to participate in development of a cyanide SSO is a continuation of the Discharger’s previous work to better to determine appropriate WQC, analytical methods, and control options for cyanide.

- Provision E.5 (Mercury Special Study):  This provision, under which the Discharger will complete a study of and evaluation of control options for mercury loadings associated with “first flush” storm water, is required to complement the interim, dry weather, effluent mass limitation for mercury.  The study results will provide useful data to support development and implementation of the mercury TMDL.

- Provision E.6 (Pretreatment Program):  The requirements to implement an approved pretreatment program are based on 40 CFR Part 403.

- Provision E.7 (Effluent Monitoring):  This provision, which requires the Discharger to conduct effluent water monitoring as provided for in the August 6, 2001 letter, is based on the Basin Plan and the SIP.

- Provision E.8 (Pollutant Prevention and Minimization Program):  This provision is based on the Basin Plan, page 4-25 – 4-28, and the SIP, Section 2.1.

- Provision E.9 (Whole Effluent Acute Toxicity):  This provision establishes conditions by which compliance with permit effluent limitations for acute toxicity will be demonstrated.  Conditions initially include the use of 96-hour bioassays, the use of rainbow trout, and the use of approved test methods as specified.  No later than November 1, 2004, the Discharger shall switch from the 3rd to  the 5th Edition USEPA protocol with flow through bioassays.  Static renewal bioassays may be allowed if the Discharger demonstrates that flow through tests are not feasible.

- Provision E.10 (Copper and Nickel Action Plans and Water Quality Attainment Strategy):  This provision incorporates the specific requirements of the May 22, 2002 Basin Plan Amendment, to implement the Water Quality Attainment Strategy, including the Copper and Nickel Action Plans.  Order 00-109, which is superceded by this Order, previously required the Discharger to implement the Copper and Nickel Action Plans.

As documented in the Staff Report for the May 22, 2002 Basin Plan Amendment, the four elements of the WQAS are:

  - Current control measures/actions to minimize copper and nickel releases (from municipal wastewater treatment plants and urban runoff programs to Lower South SF Bay;

  - Statistically-based water quality “triggers” and a receiving water monitoring program that would initiate additional control measures/actions if the “triggers” are met;

  - A proactive framework for addressing increases to future copper and nickel concentrations in Lower South SF Bay, if they occur; and

  - Metal translators that will be used to compute copper and nickel effluent limitations for the municipal wastewater treatment plans discharging to Lower South SF Bay.

- Provision E.11 (Santa Clara Basin Watershed Management Initiative):  This provision is unchanged from the previous Order and is based on BPJ.

- Provision E.12 (Receiving Water User Survey).  The long-term application of the revised bacteria limitations is contingent on completion of this survey.  These data are necessary to verify the “light” contact use of the receiving waters upon which the limitations are based.

- Provision E.13 (Dioxin Special Study):  Based on the Board’s BPJ, this study is necessary to ensure, to the extent practicable, that future dioxin monitoring will produce reliable, low level data to establish an interim limit and determine compliance with final limit.

- Provision E.14 (Optional Mass Offset):  This option is provided to encourage the Discharger to further implement aggressive reduction of mass loads to South San Francisco Bay.

- Provision E.15 (Operations and Maintenance Manual and Reliability Report), E.16 (Contingency Plan Update), and E.17 (Annual Status Reports):  These provisions are based on the Basin Plan, the requirements of 40 CFR 122, and the previous permit.

- Provision E.18. (303(d)-listed Pollutants Site-Specific Objective and TMDL Status Review):  Consistent with the SIP, the Discharger shall participate in the development of a TMDL or SSO for mercury, selenium, 4,4’-DDE, dieldrin, dioxin, and PCBs.  Active participation by the Discharger in the Clean Estuary Partnership (CEP) shall fulfill the requirements of this provision.

- Provision E.19 (Self-Monitoring Program):  The Discharger is required to conduct monitoring of the permitted discharges in order to evaluate compliance with permit conditions. Monitoring requirements are contained in the Self Monitoring Program (SMP) of the Permit.  This provision requires compliance with the SMP, and is based on 40 CFR 122.44(i), 122.62, 122.63 and 124.5.  The SMP is a standard requirement in almost all NPDES permits issued by the Board, including this Order.  It contains definitions of terms, specifies general sampling and analytical protocols, and sets out requirements for reporting of spills, violations, and routine monitoring data in accordance with NPDES regulations, the California Water Code, and Board’s policies.  The SMP also contains a sampling program specific for the facility. It defines the sampling stations and frequency, the pollutants to be monitored, and additional reporting requirements.  Pollutants to be monitored include all parameters for which effluent limitations are specified.  Monitoring for additional constituents, for which no effluent limitations are established, is also required to provide data for future completion of RPAs for them.

- Provision E.20 (Standard Provisions and Reporting Requirements):  The purpose of this provision is require compliance with the standard provisions and reporting requirements given in this Board's document titled Standard Provisions and Reporting Requirements for NPDES Surface Water Discharge Permits, August 1993 (the Standard Provisions), or any amendments thereafter.  That document is incorporated in the permit as an attachment to it.  Where provisions or reporting requirements specified in the permit are different from equivalent or related provisions or reporting requirements given in the Standard Provisions, the permit specifications shall apply.  The standard provisions and reporting requirements given in the above document are based on various state and federal regulations with specific references cited therein.

- Provision E.21 (Change in Control or Ownership):  This provision is based on 40 CFR 122.61.

- Provision E.22 (Permit Reopener): This provision is based on 40 CFR 123.

- Provision E.23 (NPDES Permit /USEPA concurrence): This provision is based on 40 CFR 123.

- Provision E.24 (Permit Expiration and Reapplication):  This provision is based on 40 CFR 122.46(a).

V.	WASTE DISCHARGE REQUIREMENT APPEALS

Any person may petition the State Water Resources Control Board to review the decision of the Board regarding the Waste Discharge Requirements.  A petition must be made within 30 days of the Board public hearing.

VI.  ATTACHMENTS

Attachment 1:  RPA Results for Priority Pollutants

Attachment 2:  Calculation of Final WQBELs

Attachment 3:  Documentation of Chromium VI, Lead, and Zinc Translator Development

ATTACMENT 3

DOCUMENTATION FOR CHROMIUM VI, LEAD, AND ZINC

TRANSLATOR DEVELOPMENT