CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN FRANCISCO BAY REGION

# SELF-MONITORING PROGRAM

FOR

CITY OF SUNNYVALE

WATER POLLUTION CONTROL PLANT

SANTA CLARA COUNTY

NPDES PERMIT NO. CA0037621

ORDER NO. R2 2003 -

Consists of:

Part A (not attached)

Adopted August 1993

And

Part B (Attached)

CONTENTS:

I.		DESCRIPTION of SAMPLING and OBSERVATION STATIONS

II.		SCHEDULE of SAMPLING, ANALYSES and OBSERVATIONS (Table 1)

III.		SPECIFICATIONS for SAMPLING, ANALYSES and OBSERVATIONS

IV.		SELECTED CONSTITUENTS MONITORING (Table 2)

V.		REPORTING REQUIREMENTS

VI.		SELF-MONITORING PROGRAM CERTIFICATION

## I.	  DESCRIPTION of SAMPLING and OBSERVATION STATIONS

A.	Influent and Intake

| Station | Description |
| --- | --- |
| A-001 | At any point in the treatment facilities headworks at which all waste tributary to the system is present. |

B.	Effluent

| Station | Description |
| --- | --- |
| E-001 | At any point in the outfall from the treatment facilities between the point of discharge and the point at which all waste tributary to that outfall is present. (May be the same as E-001-D). |
| E-001-D | At any point in the disinfection facilities at which point adequate contact with the disinfectant is assured. |

C.	Overflows and Bypasses

| Station | Description |
| --- | --- |
| OV-1 thru OV-‘n’ | Bypasses or overflows from manholes, pump stations, or collection systems. |

## II.	SCHEDULE of SAMPLING, ANALYSES AND OBSERVATIONS OF IWTP INFLUENT, EFFLUENT, AND STORM WATER OUTFALLS

The schedule of sampling, analysis and observation shall be that given in Table 1 below.

TABLE 1 - SCHEDULE of SAMPLING, ANALYSES and OBSERVATIONS   [1], [13]

| Sampling Station |  |  | A-001 | E-001D |  |  | All “OV” |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Influent | Effluent to Lower Bay |  |  | Bypass/ Overflow |
| Type of Sample |  |  | C-24 | G [2] | C-24 | Cont | O |
| Parameter | ##### Units | ##### Notes | [1] |  |  |  |  |
| Flow Rate | MGD | [3] | D |  |  | Con |  |
| CBOD520°C | mg/L & kg/day | [4] | W |  | W |  |  |
| TSS | mg/L & kg/day | [4] | W |  | W |  |  |
| Oil & Grease | mg/L & kg/day | [5] |  | Q |  |  |  |
| Settleable Matter | ml/l-hr |  |  | Q |  |  |  |
| Turbidity | NTU |  |  | D |  |  |  |
| Enterococcus | Cfu/100 ml |  |  | 5/W |  |  |  |
| Chlorine Residual & Dosage | mg/L & kg/d | [6] |  | Cont/H |  |  |  |
| Ammonia Nitrogen & Unionized Ammonia | mg/L & kg/d |  |  |  | M |  |  |
| pH | pH units |  |  | D[7] |  |  |  |
| Temperature | °C |  |  | D[7] |  |  |  |
| D.O. | mg/L & % saturation |  |  | D[7] |  |  |  |
| Dissolve Sulfides (if D.O.<5 mg/L) | mg/L |  |  | D[7] |  |  |  |
| Ammonia Nitrogen | mg/L & kg/d |  |  | W |  |  |  |
| Nitrate Nitrogen | mg/L & kg/d |  |  | W |  |  |  |
| Nitrite Nitrogen | mg/L & kg/d |  |  | W |  |  |  |
| Total Organic Nitrogen | mg/L & kg/d |  |  | W |  |  |  |
| Total Phosphate | mg/L & kg/d |  |  | M |  |  |  |
| Acute Toxicity | % Survival | [8] |  |  |  | M |  |
| Chronic Toxicity |  | [9] |  |  |  | M |  |
| Copper | µg/L |  |  | M |  |  |  |
| Mercury | µg/L | [10] |  | M |  |  |  |
| Nickel | µg/L |  |  | M |  |  |  |
| Cyanide | µg/L | [11] |  | M |  |  |  |
| Chlorodibromomethane | µg/L |  |  | M |  |  |  |
| Dichlorobromomethane | µg/L |  |  | M |  |  |  |
| Benzo(b)fluoranthene | µg/L |  |  | 2/Y |  |  |  |
| Indeno(1,2,3-cd)pyrene | µg/L |  |  | 2/Y |  |  |  |
| Tributyltin | µg/L |  |  | M |  |  |  |
| Endrin | µg/L |  |  | M |  |  |  |
| 4,4’-DDE | µg/L |  |  | 2/Y |  |  |  |
| Dieldrin | µg/L |  |  | 2/Y |  |  |  |
| Heptachlor Epoxide | µg/L |  |  | 2/Y |  |  |  |
| 2,3,7,8-TCDD and Congeners | pg/L | [12] |  | 2/Y |  |  |  |
| All Applicable Standard Observations |  |  |  | W |  |  | E |

LEGEND FOR TABLE 1

Sampling Stations:

A		=		treatment facility influent

E		=		treatment facility effluent

OV	=		overflow and bypass points

P		=		treatment facility perimeter points

Types of Samples:

C-24	=	composite sample, 24 hours (includes continuous sampling, such as for flows)

G	=	grab sample

O	=	observation

Frequency of Sampling:

Cont.	= continuous

Cont/D	= continuous monitoring & daily reporting

D = once each day

E = each occurrence

M = once each month

W = once each week

Q = once each calendar quarter

2/Y = twice each calendar year (at about 6 months intervals)

3/W = three times each calendar week (on separate days)

Parameter and Unit Abbreviations:

CBOD5 20oC  = Carbonaceous Biochemical Oxygen Demand, 5-day, at 20oC

D.O.	=	Dissolved Oxygen

TSS	=	Total Suspended Solids

mgd	=	million gallons per day

mg/L	=	milligrams per liter

ml/L-hr	=	milliliters per liter, per hour

µg/L	=	micrograms per liter

kg/day	=	kilograms per day

kg/mo	=	kilograms per month

MPN/100 ml = Most Probable Number per 100 milliliters

FOOTNOTES FOR TABLE 1

[1]		Additional details regarding sampling, analyses and observations are given in Section VI of this SMP, Specifications for Sampling, Analyses and Observations (SMP Section VI).

[2]	Grab samples shall be taken on day(s) of composite sampling.

[3]		Flow Monitoring.

Effluent flow monitoring shall be conducted by continuous measurement and influent flow shall be measured daily.  Flow shall be reported by the following measurements:

Effluent (E-001):

a.	Daily:		(1)	Average Daily Effluent Flow    (mgd)

(2)	Maximum Daily Effluent Flow  (mgd)

(3)	Minimum Daily Effluent Flow   (mgd).

b.	Monthly:   The same values as given in a. above, for the calendar month.

Influent  (A-001):

a.	Daily:		Daily Influent Flow Measurement (md)

b.	Monthly:	Daily Average, Maximum, and Minimum Flow (mgd)

[4]		The percent removal for CBOD5 and TSS shall be reported for each calendar month, in accordance with Effluent Limitation B.3

[5]		Oil & Grease Monitoring.

Each Oil & Grease sample event shall consist of a composite sample comprised of three grab samples taken at equal intervals during the sampling date, with each grab sample being collected in a glass container. The grab samples shall be mixed in proportion to the instantaneous flow rates occurring at the time of each grab sample, within an accuracy of plus or minus 5 %.  Each glass container used for sample collection or mixing shall be thoroughly rinsed with solvent rinsing as soon as possible after use, and the solvent rinsing shall be added to the composite sample for extraction and analysis.

[6]	During all times when chlorination is used for disinfection of the effluent, effluent chlorine residual concentrations shall be monitored continuously, with reporting every hour on the hour, or by grab samples taken every hour for a total of 24 chlorine residual readings a day. Grab samples may be taken by hand or by automated means using in-line equipment such as three-way valves and chlorine residual analyzers. Chlorine residual concentrations shall be monitored and reported for sampling points both prior to and following dechlorination.  Total chlorine dosage (kg/day) and dechlorination chemical dosage and/or residual shall be recorded on a daily basis.

[7]	Dissolved oxygen, temperature, and pH shall also be analyzed on the same sample(s) used for the bioassay(s) prior to starting the flow-through bioassay(s) and at intervals of 24, 48, 72, and 96 hours after starting the flow-through bioassay(s).

[8]		Acute Toxicity Monitoring (Flow-through bioassay tests).

The following parameters shall be monitored on the sample stream used for the acute toxicity bioassays, at the start of the bioassay test and daily for the duration of the bioassay test, and the results reported: flow rate, water hardness, alkalinity, pH, temperature, dissolved oxygen, and ammonia nitrogen.  If the fish survival rate in the effluent is less than 70% or the control fish survival rate is less than 90%, bioassay test shall be restarted with new batches of fish and continue back to back until compliance is demonstrated. Compliance with the toxicity limitation may be demonstrated after adjusting the effluent pH through the addition of concentrated sulfuric acid to minimize the concentration of un-ionized ammonia.

[9]		Chronic Toxicity Monitoring:  See also, Attachment A of this SMP.

1.	Chronic Toxicity Monitoring Requirements

a.	Sampling.  The Discharger shall collect 24-hour composite samples of treatment plant effluent at Sampling Station E-001, for critical life stage toxicity testing as indicated below. For toxicity tests requiring renewals, 24-hour composite samples collected on consecutive days are required.

b.	Test Species: Chronic toxicity shall be monitored by using critical life stage test(s) and the most sensitive test specie(s) identified by screening phase testing or previous testing conducted under the ETCP.  Test specie(s) shall be approved by the Executive Officer.  Two test species may be required if test data indicate that there is alternating sensitivity between the two species.

c.	Frequency:

(1) Routine Monitoring:		Monthly

(2) Accelerated Monitoring:	 Twice/Monthly, or as otherwise specified by the Executive Officer.

d.	Conditions for Accelerated Monitoring:  The Discharger shall conduct accelerated monitoring when either of the following conditions are exceeded:

(1)	Three sample median value of  1 TUc, or

(2)	Single sample maximum value of  2 TUc.

e.	Methodology:  Sample collection, handling and preservation shall be in accordance with USEPA protocols.  The test methodology used shall be in accordance with the references cited in this Permit, or as approved by the Executive Officer.  A concurrent reference toxicant test shall be performed for each test.

f.	Dilution Series:  The Discharger shall conduct tests at 12.5, 25, 50, 70, 85, and 100%. The "%" represents percent effluent as discharged.

2.  Chronic Toxicity Reporting Requirements

a. Routine Reporting:  Toxicity test results for the current reporting period shall include, at a minimum, for each test:

1.	Sample date(s)

2.  	Test initiation date

3.  	Test species

4.  	End point values for each dilution (e.g. number of young, growth rate, percent survival)

5.	NOEC value(s) in percent effluent

6.	IC15, IC25, IC40, and IC50 values (or EC15, EC25 ... etc.) in percent effluent

7.	TUc values (100/NOEC, 100/IC25, and 100/EC25)

8.	Mean percent mortality (±s.d.) after 96 hours in 100% effluent (if applicable)

9.	NOEC and LOEC values for reference toxicant test(s)

10.	IC50 or EC50 value(s) for reference toxicant test(s)

11. 	Available water quality measurements for each test (e.g., pH, D.O., temperature, conductivity, hardness, salinity, ammonia)

b. Compliance Summary:  The results of the chronic toxicity testing shall be provided in the most recent self-monitoring report and shall include a summary table of chronic toxicity data from at least eleven of the most recent samples.  The information in the table shall include the items listed above under Section [10].a, item numbers 1, 3, 5, 6(IC25 or EC25), 7, and 8.

[10]	Use ultra-clean sampling (USEPA 1669) to the maximum extent practicable, and ultra-clean analytical methods (USEPA 1631) for mercury monitoring.  The Discharger may use alternative methods of analysis (such as USEPA 245), if that alternate method has a Minimum Level of 2 ng/L or less.

[11]	The Discharger may, at their option, analyze for cyanide as Weak Acid Dissociable Cyanide using protocols specified in Standard Method Part 4500-CN-I, USEPA Method OI 1677, or equivalent alternatives in latest edition.  Alternative methods of analysis must be approved by the Executive Officer.

[12]	Data collected as part of the study required to address Provision E.13 can be provided to fulfill this dioxin monitoring requirement.  Chlorinated Dibenzodioxins and Chlorinated Dibenzofurans shall be analyzed using the latest version of USEPA Method 1613; the method shall be capable of detecting concentrations on the order of picogram per liter or lower and produce data which will allow the Board to calculate an interim limit for dioxin TEQ.  At a minimum, the Discharger is required to monitor the effluent once during the dry season and once during the wet season for the life of this permit.  Alternative  methods of analysis must be approved by the Executive Officer.

[13]	Pretreatment Program Requirements are listed in Table 2 below. Influent and effluent monitoring conducted pursuant to Table 2 above may fulfill the respective Table 3 requirements provided results are also submitted in the requisite pretreatment program reports, or results have submitted into the Electronic Reporting System (ERS).

Table 2.  Pretreatment Monitoring Requirements

| Constituents / USEPA Method | Influent | Effluent | Sludge [2] |
| --- | --- | --- | --- |
| VOC / 624 [1] | 2/Y | 2/Y | 2/Y |
| BNA / 625 [1] | 2/Y | 2/Y | 2/Y |
| Metals [3] | M | M | 2/Y |

LEGEND FOR TABLE 2

M	= once each calendar month

2/Y		= twice each calendar year (at about 6 month intervals, once in the dry season, once in the wet season)

VOC	= volatile organic compounds

BNA 	= base/neutrals and acids extractable organic compounds

FOOTNOTES FOR TABLE 2

[1]	VOC and BNA samples shall be 24-hour composite samples.  Individual grab samples shall be collected every three hours during the 24-hour sampling event, and the grab samples shall be composited in the lab just prior to analysis.

[2]	USEPA approved methods.

[3]	Same USEPA method used to determine compliance with the respective NPDES permit.  The parameters are arsenic, cadmium, chromium, copper, lead, mercury, nickel, silver, zinc, selenium and cyanide.

### III.	Monitoring Methods and Minimum Detection Levels

For compliance monitoring, analysis shall be conducted using the lowest commercially available and reasonably achievable detection levels. The intent is to provide quantification of constituents sufficient to allow evaluation of observed concentrations with respect to the minimum levels given below.

The Discharger may use the methods listed in the Table 3 below or alternate test procedures that have been approved by the U.S. EPA Regional Administrator pursuant to 40 CFR 136.4 and 40 CFR 136.5 (revised as of May 14, 1999).

Table 3:  Selected Constituents Monitoring – Minimum Levels for Toxic Pollutants

| CTR # | Constituent (a) | Minimum Level (μg/L) (b) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | GC | GCMS | LC | Color | FAA | GFAA | ICP | ICP MS | SPGFAA | HYD RIDE | CVAA | DCP |
| 6. | Copper (c) |  |  |  |  | 25 | 5 | 10 | 0.5 | 2 |  |  | 1000 |
| 8. | Mercury (d) |  |  |  |  |  |  |  | 0.5 |  |  | 0.2 |  |
| 9. | Nickel |  |  |  |  | 50 | 5 | 20 | 1 | 5 |  |  | 1000 |
| 10. | Selenium |  |  |  |  |  | 5 | 10 | 2 | 5 | 1 |  | 1000 |
| 14. | Cyanide | 0.005 |  |  | 5 |  |  |  |  |  |  |  |  |
| 23. | Chlorodibromomethane | 0.5 | 2 |  |  |  |  |  |  |  |  |  |  |
| 27. | Dichlorobromomethane | 0.5 | 2 |  |  |  |  |  |  |  |  |  |  |
| 62. | Benzo(b)fluoranthene |  | 10 | 10 |  |  |  |  |  |  |  |  |  |
| 92. | Indeno(1,2,3-cd)pyrene |  | 10 | 0.05 |  |  |  |  |  |  |  |  |  |
| 109. | 4,4’-DDE | 0.05 |  |  |  |  |  |  |  |  |  |  |  |
| 111. | Dieldrin | 0.01 |  |  |  |  |  |  |  |  |  |  |  |
| 115. | Endrin | 0.01 |  |  |  |  |  |  |  |  |  |  |  |
| 118. | Heptachlor Epoxide | 0.01 |  |  |  |  |  |  |  |  |  |  |  |

Notes:

- According to the SIP, method-specific factors (MSFs) can be applied.  In such cases, this additional factor must be applied in the computation of the reporting limit.  Application of such factors will alter the reported ML (as described in section 2.4.1)  Dischargers are to instruct laboratories to establish calibration standards so that the ML value is the lowest calibration standard.  At no time is the Discharger to use analytical data derived from the extrapolation beyond the lowest point of the calibration curve.

- Laboratory techniques are defined as follows:  GC = Gas Chromatography; GCMS = Gas Chromatography/Mass Spectrometry; LC = High Pressure Liquid Chromatography; Color = Colorimetric; FAA = Flame Atomic Absorption; GFAA = Graphite Furnace Atomic Absorption; Hydride = Gaseous Hydride Atomic Absorption; CVAA = Cold Vapor Atomic Absorption; ICP = Inductively Coupled Plasma; ICPMS = Inductively Coupled Plasma/Mass Spectrometry; SPGFAA = Stabilized Platform Graphite Furnace Atomic Absorption (i.e. USEPA 200.9); DCP = Direct Current Plasma.

- For copper, the Discharger may also use the following laboratory techniques with the relevant minimum level:  GFAA with a  minimum level of 5 μg/L and SPGFAA with a minimum level of 2 μg/L.

- Use ultra-clean sampling and analytical methods for mercury monitoring per 13267 letter issued to Discharger.  ML for compliance purposes is as listed in table above until the SWRCB adopts alternative minimum level. (see 2000 SIP Appendix 4)

- The SIP does not contain an ML for this constituent.

## IV. Specifications For Sampling, Analyses And Observations

Sampling, analyses and observations, and recording and reporting of results shall be conducted in accordance with the schedule given in Table 1 of this SMP, and in accordance with the following specifications, as well as all other applicable requirements given in this SMP. All analyses shall be conducted using analytical methods that are commercially and reasonably available, and that provide quantification of sampling parameters and constituents sufficient to evaluate compliance with applicable effluent limits.

- Influent Monitoring.

Influent monitoring identified in Table 1 of this SMP is the minimum required monitoring. Additional sampling and analyses may be required in accordance with Pretreatment Program or Pollution Prevention/Source Control Program requirements.

- Effluent Monitoring.

Composite samples of effluent shall be collected on varying days selected at random coincident with influent composite sampling unless otherwise stipulated. The Executive Officer may approve an alternative sampling plan if it is demonstrated to the Executive Officer's satisfaction that expected operating conditions for the facility warrant a deviation from the standard sampling plan.

Grab samples of effluent shall be collected during periods of maximum peak flows and shall coincide with effluent composite sample days.

Fish bioassay samples shall be collected on days coincident with effluent composite sampling.

Bioassay tests should be performed on effluent samples after chlorination-dechlorination.

Total ammonia nitrogen shall be analyzed and un-ionized ammonia calculated whenever fish bioassay test results fail to meet the specified percent survival.

If two consecutive samples within a 30 day period of a weekly or monthly monitored constituent exceed the monthly average effluent limit for any parameter, (or if the required sampling frequency is once per month and the monthly sample exceeds the monthly average limit), the sampling frequency shall be increased to daily until the additional sampling shows that the most recent 30-day moving average is in compliance with the monthly average limit.

If any maximum daily limit is exceeded, the sampling frequency shall be increased to daily until two samples collected on consecutive days show compliance with the maximum daily limit.

If the final or intermediate results of any single bioassay test indicate a threatened violation (i.e. the percentage of surviving test organisms is less than the required survival percentage), a new test will begin and the discharger shall investigate the cause of the mortalities and report the finding in the next self-monitoring report.

Chlorine residual analyzers shall be calibrated against grab samples as frequently as is necessary to maintain accurate control and reliable operation. For samples obtained hourly, in the advent of a detected effluent violation- grab samples shall be collected at least every 30 minutes until compliance is achieved.

## V. Reporting Requirements

- General Reporting Requirements are described in Section E of the Regional Board's "Standard Provisions and Reporting Requirements for NPDES Surface Water Discharge Permits", dated August 1993.

- Modifications to Self-Monitoring Program, Part A:

1.	If any discrepancies exist between Part A and Part B of the SMP, this Part B prevails.

2.	Section C.2.a of Part A, shall be modified as follows:

Composite samples of effluent as required in Table 1 of Part B shall be collected on days coincident with influent composite sampling as required in Table 1 of Part B unless otherwise stipulated.  If additional influent or effluent sampling beyond that required in Table 1 of Part B is done voluntarily or to fulfill any requirements in this permit other than those specified in Table 1 or Part B, corresponding collection of effluent or influent samples is not required by this section.  The Executive Officer may approve an alternative sampling plan if it is demonstrated to be representative of plant discharge flow and in compliance with all other requirements of this permit.

3.	Section C.2.b of Part A shall be modified as follows:

Grab samples of effluent shall be collected during periods of maximum peak flows at a frequency specified in Table 1 of Part B, shall coincide with effluent composite sample days, and shall be analyzed for the constituents specified in Table 1.

4.	The first sentence of Section C.2.c of Part A shall be replaced with:

Effluent sampling will occur on at least one day of any multiple-day flow-through bioassay test required by Table 1 in Part B.

5.	Section C.2.c(1) of Part A shall be replaced to read as follows (C.2.c(2) is unchanged):

Bioassay tests should be performed on effluent samples after chlorination-dechlorination.  If biological growth in the dechlorinated effluent sample line is a potential problem, chlorinated effluent that is dechlorinated separately from the plant dechlorination process may be used for the bioassay test.

6.	Section C.2.d. of Part A shall be modified as follows:

If two consecutive samples of a constituent monitored on a weekly or monthly basis in a 30 day period exceed the monthly average effluent limit for any parameter, (or if the required sampling frequency is once per month and the monthly sample exceeds the monthly average limit), the sampling frequency shall be repeated once within 24 hours after results are received that indicate an exceedance of the monthly average effluent limit for that parameter.  Repeat sampling shall occur in this way until the additional sampling shows two consecutive samples are in compliance with the monthly average limit.

7.	Section C.3 of Part A, insert the following:

The requirements of this section only apply to facilities where storm water is not directed to the headworks during wet weather.  At the Water Pollution Control Plant, all stormwater is directed to the headworks at all times so the requirements of this section do not apply.

8.	Section C.4 of Part A, insert the following:

The requirements of this section only apply when receiving water sampling is required by Table 1 of Part B.  Receiving water sampling is not specified in Table 1 of Part B of this permit.  Therefore, the requirements of this section do not apply.  The requirements of Section C.4. are satisfied by participation in the Regional Monitoring Program and the South Bay Monitoring Program.

9.	Section C.5 of Part A, insert the following:

The requirements of this section only apply when collection of bottom sediment samples is specified in Table 1 of Part B.  Collection of bottom sediment samples is not specified in Table 1 of Part B of this permit so the requirements of this section do not apply.

10.	Section D.1 of Part A, insert the following:

The requirements of this section only apply when receiving water standard observations are specified in Table 1 of Part B.  Receiving water standard observations are not specified in Table 1 of Part B of this permit.  Therefore, the requirements of this section do not apply.

11.	Section D.3 of Part A, insert the following:

The requirements of this section only apply when beach and shoreline standard observations are specified in Table 1 of Part B.  Beach and shoreline standard observations are not specified in Table 1 of Part B of this permit.  Therefore, the requirements of this section do not apply.

12.	Section D.5 of Part A, insert the following:

The requirements of this section only apply when facility periphery standard observations are specified in Table 1 of Part B.  Facility periphery standard observations are not specified in Table 1 of Part B of this permit.  Therefore, the requirements of this section do not apply.

13.	Section E.1 of Part A shall be modified as follows:

      - Written reports, electronic records, strip charts, equipment calibration and maintenance records, and other records pertinent to demonstrating compliance with waste discharge requirements including self-monitoring program requirements, shall be maintained by the Discharger in a manner and at a location (e.g., wastewater treatment plant or Discharger offices) such that the records are accessible to Board staff.  These records shall be retained by the Discharger for a minimum of 3 years.   The minimum period of retention shall be extended during the course of any unresolved litigation regarding the subject discharges, or when requested by the Board or by the Regional Administrator of the U.S. EPA, Region IX.  Records to be maintained shall include the following:

        - Parameter Sampling and Analyses, and Observations.

For each sample, analysis or observation conducted, records shall include the following:

          - Parameter

          - Identity of sampling or observation station, consistent with the station descriptions given in this SMP.

          - Date and time of sampling or observation.

          - Method of sampling (grab, composite, other method)

          - Date and time analysis started and completed, and name of personnel or contract laboratory performing the analysis.

          - Reference or description of procedure(s) used for sample preservation and handling, and analytical method(s) used.

          - Calculations of results.

          - Analytical method detection limits and related quantitation parameters.

          - Results of analyses or observations.

        - Flow Monitoring Data.

For all required flow monitoring (e.g., influent and effluent flows), records shall include the following:

          - Total flow or volume, for each day.

          - Maximum, minimum and average daily flows for each calendar month.

        - Wastewater Treatment Process Solids.

          - For each treatment process unit which involves solid removal from the wastewater stream, records shall include the following:

            - Total volume and/or mass quantification of solids removed from each unit (e.g., grit, skimmings, undigested sludge), for each calendar month; and

            - Final disposition of such solids (e.g., landfill, other subsequent treatment unit).

          - For final dewatered sludge from the treatment plant as whole, records shall include the following:

            - Total volume and/or mass quantification of dewatered sludge, for each calendar month;

            - Solids content of the dewatered sludge; and

            - Final disposition of dewatered sludge (point of disposal location and disposal method).

        - Disinfection Process

For the disinfection process, records shall be maintained documenting process operation and performance, including the following:

i.	For bacteriological analyses:

1.	Date and time of each sample collected

2.	Wastewater flow rate at the time of sample collection

3.	Results of sample analyses (bacteriological count)

4.	Required statistical parameters of cumulative bacteriological values (e.g., moving median or log mean for number of samples or sampling period identified in waste discharge requirements).

ii.	For chlorination process, at least daily average values for the following:

1.	Chlorine residual in contact basin (mg/L)

2.	Chlorine dosage (kg/day)

(5)	Treatment Process Bypasses

A chronological log of all treatment process bypasses, other than wet weather bypasses addressed elsewhere in this permit and self-monitoring program, including the following:

- Identification of treatment process bypassed;

- Date and time of bypass start and end;

- Total duration time;

- Estimated total volume;

- Description of, or reference to other report(s) describing, bypass event, cause, corrective actions taken, and any additional monitoring conducted.

(6)	Collection System Overflows

A chronological log of all collection system overflows, including the following:

- Location of overflow;

- Date and time of overflow start and end;

- Total duration time;

- Estimated total volume;

- Description of, or reference to other report(s) describing, overflow event, cause, corrective actions taken, and any additional monitoring conducted.

14.	Section F.1 of Part A shall be modified as follows:

      - A report shall be made of any spill of oil or other hazardous material to waters of the U.S.

      - The spill shall be reported by telephone as soon as possible and no later than 24 hours following occurrence or Discharger's knowledge of occurrence.  Spills shall be reported by telephone as follows:

        - During weekdays, during office hours of 8 am to 5 pm, to the Regional Board:

Current phone number: 	(510) 622 - 2300.

Current Fax number:	(510) 622 - 2460.

        - During non-office hours, to the State Office of Emergency Services:

Current phone number: (800) 852 - 7550.

      - A written report shall be submitted to the Regional Board within five (5) working days following telephone notification, unless directed otherwise by Board staff.  A report submitted by facsimile transmission is acceptable for this reporting.  The written report shall include the following:

        - Date and time of spill, and duration if known.

        - Location of spill (street address or description of location).

        - Nature of material spilled.

        - Quantity of material involved.

        - Receiving water body affected.

        - Cause of spill if determined.  If not yet determined, then a statement of potential cause(s) and action(s) taken to determine ultimate cause.  Include date when final report will be submitted on this issue.

        - Observed impacts to receiving waters (e.g., discoloration, oil sheen, fish kill).

        - Corrective actions that were taken to contain, minimize or cleanup the spill.

        - Future corrective actions planned to be taken in order to prevent recurrence, and time schedule of implementation.

        - Persons or agencies contacted.

15.	Section F.4 of Part A shall be modified as follows:

For each calendar month, a self-monitoring report (SMR) shall be submitted to the Board in accordance with the following:

      - The report shall be submitted to the Board no later than 45 days from the last day of the reporting month.

      - Letter of Transmittal

Each report shall be submitted with a letter of transmittal.  This letter shall include the following:

        - Identification of all violations of effluent limits or other discharge requirements found during the monitoring period;

        - Details of the violations: parameters, magnitude, test results, frequency, and dates;

        - The cause of the violations;

        - Discussion of corrective actions taken or planned to resolve violations and prevent recurrence, and dates or time schedule of action implementation. If previous reports have been submitted that address corrective actions, reference to such reports is satisfactory.

        - Signature:	The letter of transmittal shall be signed by the Discharger's principal executive officer or ranking elected official, or duly authorized representative, and shall include the following certification statement:

"I certify under penalty of law that this document and all attachments have been prepared under my direction or supervision in accordance with a system designed to assure that qualified personnel properly gathered and evaluated the information submitted.  The information submitted is, to the best of my knowledge and belief, true, accurate and complete.  I am aware that there are significant penalties for submitting false information, including the possibility of fine and imprisonment."

      - Compliance Evaluation Summary

Each report shall include a compliance evaluation summary.  This summary shall include, for each parameter for which effluent limits are specified in the Permit, the number of samples taken during the monitoring period, and the number of samples in violation of applicable effluent limits.

      - Results of Analyses and Observations.

        - Tabulations of all required analyses and observations, including parameter, sample date and time, sample station, and test result.

        - If any parameter is monitored more frequently than required by this permit and SMP, the results of this additional monitoring shall be included in the monitoring report, and the data shall be included in data calculations and compliance evaluations for the monitoring period.

        - Calculations for all effluent limits that require averaging of measurements shall utilize an arithmetic mean, unless specified otherwise in this permit or SMP.

      - Data Reporting for Results Not Yet Available.

The Discharger shall make all reasonable efforts to obtain analytical data for required parameter sampling in timely manner.  The Board recognizes that certain analyses require additional time in order to complete analytical processes and result reporting.  For cases where required monitoring parameters require additional time to complete analytical processes and reporting, and results are not available in time to be included in the SMR for the subject monitoring period, such cases shall be described in the SMR.  Data for these parameters, and relevant discussions of any observed violations, shall be included in the next SMR due after results are available.

- Reporting Data in Electronic Format.

The Discharger has the option to submit all monitoring results in an electronic reporting format approved by the Executive Officer.  The discharger is currently submitting SMRs electronically in a format approved by the Executive Officer in a letter dated December 17, 1999, Official Implementation of Electronic Reporting System (ERS). The ERS format includes, but is not limited to, a transmittal letter, summary of violation details and corrective actions, and transmittal receipt.  If there are any discrepancies between the ERS requirements and the “hard copy” requirements listed in the SMP, then the approved ERS requirements supercede.

16.	Section F.5 of Part A shall be modified as follows

An Annual Report shall be submitted for each calendar year. The report shall be submitted to the Regional Board by the last day of February of the following year.  This report need not be submitted if all data has previously been submitted electronically.  This report shall include the following:

  - Both tabular and graphical summaries of monitoring data collected during the calendar year that characterizes treatment plant performance and compliance with waste discharge requirements.

  - A comprehensive discussion of treatment plant performance and compliance with waste discharge requirements. This discussion should include any corrective actions taken or planned such as changes to facility equipment or operation practices which may be needed to achieve compliance, and any other actions taken or planned that are intended to improve performance and reliability of the discharger's wastewater collection, treatment or disposal practices.

  - A plan view drawing or map showing the dischargers' facility, flow routing and sampling and observation station locations.

17.	Section G. of Part A, Definition of Terms, amend as follows:

- Grab Sample.  A grab sample is defined as an individual sample collected in a short period of time not exceeding fifteen minutes.   A grab sample represents only the conditions that exist at the time the sample is collected.  Grab samples shall be collected during normal peak loading conditions for the parameter of interest, which may not necessarily correspond with periods of peak hydraulic conditions.  Grab samples are used primarily in determining compliance with daily and instantaneous maximum or minimum.

- Composite Sample.   A composite sample is defined as a sample composed of individual grab samples collected manually or by an autosampling device on the basis of time and/or flow as specified in Table 1 of Part B.  For flow-based compositing, the proportion of each grab sample included in the composite sample shall be within plus or minus five percent from the representative flow rate of the waste stream being sampled measured at the time of grab sample collection.  Alternately, equal volume grab samples may be individually analyzed and the flow-weighted average calculated by averaging flow-weighted ratios of each grab sample analytical result.  Grab samples forming time-based composite samples shall be collected at intervals not greater than those specified in Table 1 of Part B.  The quantity of each grab sample forming a time-based composite sample shall be a set or flow proportional volume as specified in Table 1 of Part B.  For Oil and Grease, a minimum of three grab samples, one every eight hours over a 24-hour period shall be used.  If a particular time or flow-based composite sampling protocol is not specified in Table 1 of Part B, the Discharger shall determine and implement the most representative sampling protocol for the given parameter subject to approval by the Executive Officer.

- Average.  Average values for daily and monthly values are obtained by taking the sum of all daily values divided by the number of all daily values measured during the specified period.  In calculating the monthly average, when there is more than one value for a given day, all the values.

## VI.	 SELF-MONITORING PROGRAM CERTIFICATION

I, Loretta K. Barsamian, Executive Officer, hereby certify that the foregoing Self-Monitoring Program:

1.  	Has been developed in accordance with the procedure set forth in this Board's Resolution No. 73-16 in order to obtain data and document compliance with waste discharge requirements established in Board Order No. 03-    .

2.  	May be reviewed at any time subsequent to the effective date upon written notice from the Executive Officer or request from the Discharger, and revisions will be ordered by the Executive Officer.

3.  	Is effective as of                    , 2002.

____________________________________

LORETTA K. BARSAMIAN

Executive Officer

Attachment A:  Chronic Toxicity – Definition of Terms and Screening Phase Requirements

ATTACHMENT A

CHRONIC TOXICITY

DEFINITION OF TERMS & SCREENING PHASE REQUIREMENTS

I.	Definition of Terms

A.	No observed effect level (NOEL) for compliance determination is equal to IC25 or EC25.  If the IC25 or EC25 cannot be statistically determined, the NOEL shall be equal to the NOEC derived using hypothesis testing.

B.	Effective concentration (EC) is a point estimate of the toxicant concentration that would cause an adverse effect on a quantal, "all or nothing," response (such as death, immobilization, or serious incapacitation) in a given percent of the test organisms.  If the effect is death or immobility, the term lethal concentration (LC) may be used.  EC values may be calculated using point estimation techniques such as probit, logit, and Spearman-Karber.  EC25 is the concentration of toxicant (in percent effluent) that causes a response in 25% of the test organisms.

C.	Inhibition Concentration (IC) is a point estimate of the toxicant concentration that would cause a given percent reduction in a non-lethal, non-quantal biological measurement, such as growth.  For example, an IC25 is the estimated concentration of toxicant that would cause a 25% reduction in average young per female or growth.  IC values may be calculated using a linear interpolation method such as USEPA's Bootstrap Procedure.

D.	No observed effect concentration (NOEC) is the highest tested concentration of an effluent or a toxicant at which no adverse effects are observed on the aquatic test organisms at a specific time of observation.  It is determined using hypothesis testing.

II.	Chronic Toxicity Screening Phase Requirements

A.	The Discharger shall perform screening phase monitoring:

1.	Subsequent to any significant change in the nature of the effluent discharged through changes in sources or treatment, except those changes resulting from reductions in pollutant concentrations attributable to pretreatment, source control, and waste minimization efforts, or

2.	Prior to Permit reissuance.  Screening phase monitoring data shall be included in the NPDES Permit application for reissuance.  The information shall be as recent as possible, but may be based on screening phase monitoring conducted within 5 years before the permit expiration date.

B.	Design of the screening phase shall, at a minimum, consist of the following elements:

1.	Use of test species specified in Tables 1 and 2 (attached), and use of the protocols referenced in those tables, or as approved by the Executive Officer;

2.	Two stages:

a.	Stage 1 shall consist of a minimum of one battery of tests conducted concurrently.  Selection of the type of test species and minimum number of tests shall be based on Table 3 (attached); and

b.	Stage 2 shall consist of a minimum of two test batteries conducted at a monthly frequency using the three most sensitive species based on the Stage 1 test results and as approved by the Executive Officer.

3.	Appropriate controls; and

4.	Concurrent reference toxicant tests.

C.	The Discharger shall submit a screening phase proposal to the Executive Officer for approval.  The proposal shall address each of the elements listed above.

TABLE C 1

CRITICAL LIFE STAGE TOXICITY TESTS FOR ESTUARINE WATERS

___________________________________________________________________________________________

TEST	REFER-

SPECIES	(Scientific name)	EFFECT	DURATION   	ENCE

___________________________________________________________________________________________

alga	(Skeletonema costatum)	growth rate	 4 days		1

(Thalassiosira pseudonana)

red alga	(Champia parvula)	number of cystocarps	7-9 days		5

Giant kelp	(Macrocystis pyrifera)	percent germination;	48 hours		3

germ tube length

abalone	(Haliotis rufescens)	abnormal shell development	48 hours		3

oyster 	(Crassostrea gigas)	{abnormal shell development;	48 hours		2

mussel 	(Mytilus edulis)	{percent survival

Echinoderms		percent fertilization	 1 hour		4

(urchins - 	Strongylocentrotus purpuratus,

S. franciscanus);

(sand dollar - Dendraster excentricus)

shrimp	(Mysidopsis bahia)	percent survival;  growth;	 7 days		5

fecundity

silversides	(Menidia beryllina)	larval growth rate;	 7 days		5

percent survival

___________________________________________________________________________________________

Toxicity Test References:

1.	American Society for Testing Materials (ASTM).  1990.  Standard Guide for conducting static 96-hour toxicity tests with microalgae. Procedure E 1218-90. ASTM Philadelphia, PA.

2.	American Society for Testing Materials (ASTM).  1989.  Standard Practice for conducting static acute toxicity tests with larvae of four species of bivalve molluscs.  Procedure E 724-89.  ASTM, Philadelphia, PA.

3.	Anderson, B.B. J.W. Hunt, S.L. Turpen, A.R. Coulon, M. Martin, D.L. McKeown, and F.H. Palmer.  1990.  Procedures manual for conducting toxicity tests developed by the marine bioassay project.  California State Water Resources Control Board, Sacramento.

4.	Dinnel, P.J., J. Link, and Q. Stober.  1987.  Improved methodology for sea urchin sperm cell bioassay for marine waters.  Archives of Environmental Contamination and Toxicology 16:23-32.  and  S.L. Anderson.  Sept. 1, 1989.  Technical Memo.  San Francisco Bay Regional Water Quality Control Board, Oakland, CA.

5.	Weber, C.I., W.B. Horning, II, D.J. Klem, T.W. Neiheisel, P.A. Lewis, E.L. Robinson, J. Menkedick, and F. Kessler (eds.).  1988.  Short-term methods for estimating the chronic toxicity of effluents and receiving waters to marine and estuarine organisms.  USEPA-600/4-87/028.  National Technical Information Service, Springfield, VA.

TABLE C 2

CRITICAL LIFE STAGE TOXICITY TESTS FOR FRESH WATERS

________________________________________________________________________________

SPECIES	(Scientific name)	EFFECT             TEST DURATION     REFERENCE

________________________________________________________________________________

fathead minnow	(Pimephales promelas)       	survival;	     7 days		       6

growth rate

water flea	(Ceriodaphnia dubia)	survival;	     7 days		       6

number of young

alga		(Selenastrum capricornutum)	cell division rate	     4 days		       6

________________________________________________________________________________

Toxicity Test Reference:

6.	Horning, W.B. and C.I. Weber (eds.).  1989.  Short-term methods for estimating the chronic toxicity of effluents and receiving waters to freshwater organisms.  Second edition.  USEPA Environmental Monitoring Systems Laboratory, Cincinnati, Ohio.  USEPA/600/4-89/001.

--------------------------------------------------------------------------------------------------------------------------------------

TABLE C 3

TOXICITY TEST REQUIREMENTS FOR STAGE ONE SCREENING PHASE

| REQUIREMENTS | RECEIVING WATER CHARACTERISTICS |  |  |
| --- | --- | --- | --- |
|  | Discharges to Coast | Discharges to San Francisco Bay ‡ |  |
|  | Ocean | Marine | Freshwater |
| Taxonomic Diversity: | 1 plant 1 invertebrate 1 fish | 1 plant 1 invertebrate 1 fish | 1 plant 1 invertebrate 1 fish |
| Number of tests of each salinity type: Freshwater (†): Marine: | 0 4 | 1 or 2 3 or 4 | 3 0 |
| Total number of tests: | 4 | 5 | 3 |

†	The fresh water species may be substituted with marine species if:

1)	The salinity of the effluent is above 5 parts per thousand (ppt) greater than 75% of the time, or

2)	The ionic strength (TDS or conductivity) of the effluent at the test concentration used to determine compliance is documented to be toxic to the test species.

‡	Marine refers to receiving water salinities greater than 5 ppt at least 75% of the time during a normal water year.

Fresh refers to receiving water with salinities less than 5 ppt at least 75% of the time during a normal water year.