### Attachment 1 – Determination of Technology-Based Requirements

Determination of Technology-Based Requirements for NPDES Permit No. CA0037681: Westside Wet-Weather Facilities and Southwest Ocean Outfall, City and County of San Francisco.

The Clean Water Act (CWA) established the National Pollutant Discharge Elimination System (NPDES) permit program to regulate all point source discharges to the nation's waters.  All dischargers must comply with two sets of requirements:  (1) technology-based minimum requirements that apply to all dischargers of a specified class or (2) more stringent effluent limits, if necessary, to meet local water quality standards (WQSs). (CWA, Section 301(b)).  Thus, effluent discharge permit limitations are either technology-based or water quality based.  The technology-based requirements for non-POTW discharges (such as Combined Sewer Overflows (CSOs)) must reflect:

1.	Best Practicable Control Technology Currently Available (BPT):  The basic control level that all discharges (other than POTWs) must attain.  BPT was the initial technology-based control level required by the CWA and usually reflected the average of the best existing performance in a category.  This treatment level is determined first and then used in calculating the following two control levels, which may be more stringent.

2.	Best Conventional Pollutant Control Technology (BCT):  Treatment that may be applied in addition to BPT for removal of conventional pollutants such as suspended solids, biochemical oxygen demand, oil and grease, pH, and coliform bacteria.

3.	Best Available Technology Economically Achievable (BAT):  Treatment that may be applied in addition to BPT for removal of toxic pollutants and other non-toxic,  non-conventional pollutants such as floatables.

EPA establishes some technology-based requirements by issuing industry-wide effluent guidelines.  For CSOs, no effluent guidelines have been promulgated for BPT, BCT, or BAT.  The permit writer must therefore use Best Professional Judgement (BPJ) to determine the level of treatment that BPT, BCT and BAT represent and must establish limits to ensure these levels of treatment.

The San Francisco CSO control and treatment program includes a combination of containment and treatment facilities in addition to non-structural controls.  (See fact sheet for Westside permit and Section II.A.ii of this permit for a detailed description of San Francisco’s Westside CSO facilities).  There are also a number of discharge locations.  The technology-based controls (BPT, BCT, BAT) are applicable to the following elements of San Francisco's Westside Combined Sewer System as follows:

# Oceanside Water Pollution Control Plant

The Oceanside Water Pollution Control Plant (Oceanside WPCP) is a Publicly Owned Treatment Works (POTW) recently brought on-line to replace an outmoded secondary treatment facility.  All flows directed to this POTW must receive treatment to the secondary standards identified in the regulations (40 CFR 133) (except for flows which meet the definition of an authorized "bypass" as discussed in Section I.4 below).  The BPT/BCT/BAT analysis is therefore not applicable to the discharge from the Oceanside WPCP since the secondary standards establish the technology-based treatment requirements.

Flow-through Treatment in the Storage/Transports with Discharge to the Southwest Ocean Outfall ("Decant")

The wastewater from the storage/transports discharged directly (after flow-through treatment) to the Southwest Ocean Outfall (SWOO) does not enter the Oceanside Water Pollution Control Plant, and, therefore, is not subject to secondary treatment requirements.  See In the Matter of City & County of San Francisco, NPDES Appeal No. 91-18.  Instead, this discharge must meet BPT/BAT/BCT-based limits established using BPJ.  This discharge is defined as a Combined Sewer Overflow (CSO).

Flow-through Treatment in the Storage/Transports with Discharge to the Shoreline

This wastewater discharged from the storage/transports (after flow-through treatment) to the shoreline also does not enter the Oceanside Treatment Plant, and, therefore, is not subject to secondary treatment requirements.  Instead, this discharge must meet BPT/BCT/BAT-based limits established using BPJ.  This discharge is also defined as a CSO.

Summary of Analysis:

In Section I of this document, the U.S. Environmental Protection Agency (EPA) Region IX examines the nine minimum controls established in the 1994 CSO Policy.  EPA concludes that these measures are a cost-effective means for achieving effluent reductions of both conventional and non-conventional pollutants.  EPA also concludes that implementation of these measures is consistent with the treatment processes and engineering systems employed by San Francisco and would result in no deleterious non-water quality environmental impacts.  Therefore, these measures pass the BPT/BCT/BAT cost test.  The NPDES permit for CSO discharges from the Southwest Ocean Outfall therefore establishes the nine minimum controls as technology-based requirements and will contain provisions to ensure compliance with these controls.

In Section II of this document, EPA performs a BPJ analysis for the City of San Francisco's Combined Sewer System discharge from the Southwest Ocean Outfall and concludes:

a.	The system currently in place provides effluent reduction at a cost in excess of that which would be required by BPT/BCT/BAT; and

b.	No additional treatment facilities can be justified on a BPT/BCT/BAT cost basis.

The NPDES permit for Westside CSO discharges to be issued jointly by EPA and the Regional Water Quality Control Board (the Board or RWQCB) will include requirements to ensure proper operation of the existing CSO facilities.  This will provide treatment in excess of that which would be required based on BPT/BCT/BAT requirements.  This analysis also provides EPA Region IX's reconsideration of whether effluent limitations based on increased storage of wet weather flows can be justified on a BAT or BCT basis.  EPA Region IX proposed to carry out this analysis when it withdrew portions of the previous NPDES permit.

In conclusion, by including requirements in the draft NPDES permit to ensure the continued implementation of the nine measures outlined in the CSO Policy and to require proper operation of the existing CSO facilities, EPA has established the technology-based requirements mandated by the Clean Water Act.

I.	Establishment of the Nine Minimum Controls as Minimum BCT/BAT Requirements:

EPA adopted a CSO Policy which provides guidance to the permit writer. 59 Fed. Reg. 18688 (April 19, 1994).  This CSO Policy was developed with extensive input from key stakeholders including representatives from States, environmental groups, and municipal organizations.  The policy establishes a consistent approach for controlling discharges from CSOs to the Nation's waters through the NPDES program.  The nine minimum controls outlined in the CSO Policy were developed after extensive review of existing CSO control systems, the cost of the controls and the effectiveness of the technologies.  Though the CSO Policy has not been promulgated as a federal regulation, the nine minimum controls are often established as BAT/BCT requirements.  This approach is consistent with EPA's 1994 CSO Policy, which states (Section IV. Expectations for Permitting Authorities):

All permits for CSO discharges should require the nine minimum controls as a minimum best available technology economically achievable and best conventional technology (BAT/BCT) established on a best professional judgment (BPJ) basis by the permitting authority (40 CFR Section 125.3).

These nine measurements are as follows:

1.	Proper operation and regular maintenance

2.	Maximum use of the collection system for storage

3.	Review and modification of pretreatment programs

4.	Maximization of flow to the POTW for treatment

5.	Prohibition of dry weather overflows

6.	Control of solid and floatable materials in CSO discharges

7.	Pollution prevention programs

8.	Public notification

9.	Monitoring

Thus, pursuant to the Policy, these nine minimum controls will constitute the minimum technology as required by Section 301(b)(2) of the Clean Water Act.  The EPA and Board staff, based on their best professional judgment, have determined that these controls can be appropriately applied to the discharger.  Furthermore, an evaluation of the City's consistency with the nine minimum control technologies shows that the City has met or exceeded each technology.

The following text describes how San Francisco has implemented each of the nine control technologies and describes the permit conditions that ensure future consistency with these objectives.  Finally, each control is identified as a BCT control (for the removal of conventional pollutants) and/or at BAT control (for the removal of toxic and/or non-conventionals including floatables.  (See Part II for a more detailed discussion of BPT, BCT, and BAT).

1.	Proper Operation and Regular Maintenance:  Proper operation and maintenance of Combined Sewer Systems (CSSs) decreases pollutant loadings that occur during wet-weather events.  Solids can settle out of the sewage and collect in the large combined sewers during dry-weather periods; these solids can become remobilized and flushed from the combined system by the first storm, or the so-called "first flush" phenomenon.  San Francisco's hilly topography minimizes the amount of sewage solids that settle out of the wastewater.  Sewer system inspection and maintenance ensures that breaks and blockages do not occur when the system is fully charged, as it is during storm events.  Operation and maintenance of the City's CSS fall within the purview of three bureaus within the City's Department of Public Works:  the Bureau of Street and Sewer Repair, the Bureau of Water Pollution Control, and the Bureau of Engineering.  The City has an aggressive program of sewer system maintenance, including cleaning sewer pipes and catch basins, repairing main and side sewers, relieving flooded catch basins and plugged main sewers, and investigating public requests.  The City also has a program whereby television cameras are routed through sewer lines to visually inspect lines for breaks, illegal connections, etc.

Operation and maintenance procedures for the City's Westside Facilities are described in the City's Westside Operation Plan.  The system allows for combined flows to be routed first to the Oceanside Water Pollution Control Plant or stored in the Westside Transport for later treatment; decanted discharge can also be pumped to the Southwest Ocean Outfall for ocean disposal.  Only after these steps have been taken are overflows of decanted combined effluent discharged to the near-shore waters.  Procedures described in the Operation Plan ensure that the system operates as it was designed and constructed.

The draft NPDES permit requires that the City review and update its Operations and Maintenance Manual annually.  This manual is subject to the review and approval of EPA.   This requirement represents both a BCT and BAT control because it results in the removal of conventional, toxic and non-conventional pollutants.

2.	Maximum Use of the Collection System for Storage:  This requirement refers to the use of existing sewers to hold a portion of surplus flows during storm events.  To the extent allowed by existing facilities, this has always been San Francisco's policy.  The City's hilly terrain, however, previously limited the ability of the sewer system to store flows.  The storage/transport construction program has increased the citywide storage capacity of existing sewers to an estimated 23 MG.

The Westside facilities provide for the temporary storage of about 70 MG of combined flows that exceed the treatment plant capacity.  This amount of storage is sufficient to hold all runoff from a rainfall event of approximately 0.52 inches.  Stored wastewater is treated after the storm flow subsides.  Only after the storage facilities are filled to capacity and the treatment plants are operating at full capacity does an overflow to the beach occur.  The storage in both the sewers themselves and the system as a whole is therefore maximized before an overflow event occurs.  However, it should be noted that the storage/transport facilities were constructed as necessary components of the Master Plan to meet water quality standards.  The increased storage of 23 MGD in the existing sewers is an incidental benefit.  Minimum technology #2 refers to sewer system storage rather than the large volume storage provided by the storage/transports.

Since the maximization of collection system for storage is inherent in the design of these facilities, no NPDES permit condition is necessary to ensure future consistency with this provision other than the standard NPDES permit conditions requiring proper operation and maintenance and prohibiting unnecessary bypass of treatment facilities.  The maximization of the collection system for storage  represents both a BCT and BAT control because it results in the removal of conventional, toxic and non-conventional pollutants.

3.	Review and Modification of Pretreatment Requirements:  Pretreatment programs limit the amount of toxic pollutants discharged to the sewer system from industries and related sources.  San Francisco has an approved and fully functioning Industrial Waste Pretreatment Program, including the establishment of Local Limits for several pollutants.  Although San Francisco has relatively few industrial sources (particularly on the Westside), the City has an ongoing effort to identify industrial and other pollutant sources and reduce the loading of  toxic pollutants and other pollutants of concern.  This program, administered by the City's Bureau of Environmental Regulation and Management (BERM), includes enforcement inspections, pretreatment monitoring, collection system monitoring, and permitting of Significant Industrial Users (SIUs).

The main dischargers of toxic pollutants to the Westside system are hospitals and other medical facilities, with lesser amounts contributed by laundry, photographic, and car wash facilities.  Laboratory analysis indicates the presence of copper, lead, mercury, nickel, silver, zinc, and PAHs in wet-weather effluent from the Richmond-Sunset Water Pollution Control Plant (RSWPCP).  Most of these pollutants are believed to originate from motor vehicles and would therefore be unaffected by pretreatment programs.

The draft NPDES permit requires the implementation, review and modification of pretreatment requirements.  This requirement represents a BAT control because it results primarily in the removal of toxic pollutants.

4.	Maximization of Flow to the POTW for Treatment:  This requirement refers to operating treatment plants at maximum capacity during storm events.  This requirement has always been San Francisco's policy.  The City's system has been designed and constructed to maximize flows to the Oceanside Water Pollution Control Plant.  The Oceanside WPCP recently replaced the RSWPCP, constructed in 1938, which provided a maximum of 45 million gallons per day (MGD) of primary treatment capacity.  The Oceanside WPCP provides up to 43 MGD of secondary treatment capacity (average dry-weather flow is about 24 MGD), and another 22 MGD of primary treatment capacity during wet-weather periods, for a total treatment capacity of 65 MGD during wet weather.  Treated effluent is combined prior to discharge to the Pacific Ocean via the Southwest Ocean Outfall (SWOO).  Flows to the Oceanside WPCP are maximized prior to any discharge of decant from the Westside Transport to either the SWOO or to the near-shore waters of the Pacific Ocean.

While the City can treat 65 MGD of flow to primary levels at the Oceanside WPCP, the plant can provide secondary treatment for only 43 MGD.  Thus, when wet weather flow exceed 43 MGD, Oceanside WPCP is designed to allow excess flows (between 43 MGD and 65 MGD) to bypass the secondary treatment processes and discharge to the SWOO after receiving only primary treatment.  The CSO Policy describes the circumstances where such bypassing may be explicitly authorized in a CSO permit.  59 Fed. Reg. 18693.

For such bypassing to be permitted, the permittee must justify the cut-off point at which the flow will be diverted from the secondary treatment portions of the treatment plant, and provide a benefit-cost analysis demonstrating that the conveyance of wet weather flow to the POTW for primary treatment is more beneficial than other CSO abatement alternatives such as storage and pump back for secondary treatment, sewer separation, or satellite treatment.

The City performed a benefit-cost on CSO abatement alternatives as part of its 1972 Master Plan.  The system currently being implemented was determined to be significantly more beneficial than any of the other options analyzed.  In particular, the Master Plan determined that sewer separation was extremely costly, highly disruptive, and undesirable in that it would not address stormwater pollution.  In addition, the analysis performed as part of this permit demonstrates that providing either additional storage (to increase secondary treatment of stored wastewater) or additional secondary treatment capacity is both extraordinarily expensive and highly disruptive to the local community.  EPA therefore concludes that no further wet-weather storage or treatment can be justified.

In addition, the permittee must demonstrate compliance with the requirements of 40 CFR 122.41(m)(4) for the bypass to be permitted.  The bypass must be unavoidable to prevent loss of life, personal injury or severe property damage.  For purposes of CSO permits, severe property damage includes situations where flows above a certain level wash out the POTW's secondary treatment system.  See 59 Fed. Reg. 18694.  Also, there must be no feasible alternatives to the bypass.  For purposes of CSO permits, this provision is met if:

a.	the secondary treatment system is properly operated and maintained;

b.	the secondary system has been designed to meet secondary limits for flows greater than peak dry weather flow, plus an appropriate quantity of wet weather flow; and

c.	it is either technically or financially infeasible to provide secondary treatment at the existing facilities for greater amount of wet weather flow.

Finally, the permittee must provide notice of the need for the bypass.  This last provision is satisfied by the City's NPDES permit application describing the Oceanside WPCP facilities and its wet-weather operation plans.

The Oceanside WPCP can provide 43 MGD of secondary treatment nearly double the peak dry weather flow of 24 MGD.  If the City attempts to provide secondary treatment to more than 43 MGD of flow during wet weather, the City risks washing out its biological treatment processes.  This would result in serious property damage at the Oceanside WPCP.  In addition, it would degrade treatment performance significantly until the biological treatment process could be reestablished.  The Master Plan for the City's Westside facilities documents the financial infeasibility of providing more secondary treatment capacity for wet weather flows at the OWPCP.  This is confirmed by EPA's BPT/BCT/BAT Cost Analysis. ( See Section I). In addition, the location of the Oceanside WPCP near the San Francisco Zoo is physically limited.  Expansion of the treatment works on site is essentially impossible without severe disruption to zoo facilities.

The draft permit requires compliance with this objective.  It requires the City to provide secondary treatment for all flows reaching the Oceanside WPCP up to 43 MGD.  For flows up to 65 MGD, the City must provide primary treatment at the Oceanside WPCP for the flows in excess of 43 MGD.  In addition, the City is required to use the storage capacity in the Westside Transport to maximize, to the extent feasible, storage of wet weather flows for later treatment during dry weather periods.  This requirement represents both a BCT and BAT control because it results in the removal of conventional, toxic and non-conventional pollutants.

5.	Prohibition of Dry-Weather Overflows:  Previous wastewater permits issued to the City have prohibited dry-weather discharge of untreated wastewater from the CSS.  Even prior to the Master Plan construction program, the system was designed to hold and treat all dry weather flow.  The Westside Transport has enough storage capacity to provide for about three days of dry weather flow.  After the 1989 Loma Prieta earthquake, the RSWPCP was without electrical power for more than one day.  All wastewater generated in the Westside service area during the power outage was stored in the Westside Transport and subsequently treated.

The draft NPDES permit prohibits dry-weather overflows.  This requirement represents both a BCT and BAT control because it results in the removal of conventional, toxic and non-conventional pollutants.

6.	Control of Solid and Floatable Materials in CSO Discharges:  Control technologies assumed as part of the 1986 Strategy include, for example, baffles to control floatables and screening or swirl concentrators to control solids.  These technologies remove aesthetically objectionable materials that would otherwise remain on beaches or float on water surfaces after a storm; they have little effect, however, on suspended solids or bacterial loading of the overflows.  Rotary screening provides only about five percent total suspended solids (TSS) removal, and swirl concentrators provide about 15 percent removal.

The City's storage/transport system provides a substantially higher level of control of solid and floatable materials in CSO decant discharged to the Bay, the SWOO, and to near-shore waters of the Pacific Ocean.  Baffles control floatables, and the flow is passed over a weir to remove settleable solids.  A study was conducted to determine the solids removal efficiency of the Westside Transport, which concluded that the performance of the Transport was not markedly different from that of a primary treatment plant, providing between 15 and 50 percent removal of TSS; the baffling system was shown to retain the majority of the macroscopic floatable material that entered the Transport.  Beach deposition of CSO floatables has therefore been largely eliminated.

Because the design of the facilities ensures continual consistency with this objective, there is no need for any additional permit requirement other than the standard NPDES permit conditions requiring proper operation and maintenance and prohibiting unnecessary bypass of treatment facilities.  The baffled storage/transport represents both a BCT and BAT control because it results in the removal of conventional, toxic and non-conventional pollutants.

7.	Pollution Prevention:  Pollution prevention is source reduction and other practices that reduce or eliminate pollutants through the increased efficiency in the use of resources or the protection of resources by conservation.  Two major source reduction efforts implemented by the City's BERM focus on reducing the pollutants released to the environment through the sewer system:  (1) the development of an overall pollution prevention program and (2) the implementation of a wastewater waste minimization program as part of the pretreatment requirements.  The City's proactive water pollution prevention and pretreatment programs, managed by BERM, minimize the introduction of toxic pollutants into the CSS.  (The pretreatment program is discussed in greater detail under Item 3 above.)

The City undertook a study of Best Management Practices (BMPs) to determine which would provide the most cost-effective reduction in pollutant loadings into the CSS during both dry- and wet-weather periods.  The most important pollutants of concern during wet-weather periods include PAHs, copper, lead, and cyanide.  The main sources of these pollutants are automobiles and automotive-related businesses; other sources include tar shingles, wood preservatives, paints, algicides, and manufacturing.

A key BMP is the City's street sweeping program, which directly reduces pollutants originating from street surfaces; all City streets are swept at least once per week with vacuum sweepers.  Catch basins are also cleaned regularly to reduce the pollutant loading during storm events.  Other BMPs selected for implementation include an education program and provision of alternative disposal methods for residential hazardous waste, regulatory measures to reduce the risk of toxic spills, and public agency measures to prevent contact of rainfall runoff with potential contaminants.

Table 1 illustrates the total estimated pollutant reduction that could occur from implementation of the City's source reduction strategies.  Note that these are estimates, and reductions could increase if previously unknown pollutant sources are identified and targeted for source reduction strategies.

The draft NPDES permit requires the implementation and continual development of a Pollution Prevention Plan.  This plan is subject to the review and approval of EPA.  This requirement represents a BAT control because it primarily results in the removal of toxic pollutants.

| 8. Public Notification: The City has a long-term practice of posting notices along the shoreline for three days following any shoreline discharge. When a CSO event occurs, the City posts notices on beaches in the vicinity of the overflow warning the public that waters contain high levels of bacteria and may therefore be unsuitable for water contact recreation. Warning signs remain posted until monitoring indicates that bacteriological levels are within an acceptable range. Additionally, if a shoreline discharge occurs, or if routine monitoring indicates high bacteriological levels, the City notifies the surfing and windsurfing communities through a recorded hotline, warning that waters are unsafe and surfing is not recommended. When bacterial counts have returned to safe levels, this message is discontinued. Pollutant | Estimated Reductions |  |
| --- | --- | --- |
|  | lbs/dy | mg/l |
| Copper (Cu) | 14.7 | 0.0027 |
| Mercury (Hg) | 0.16 | 0.0003 |
| Lead (Pb) | 3.7 | 0.007 |
| Nickel (Ni) | 1.9 | 0.004 |
| Silver (Ag) | 2.2 | 0.004 |
| Zinc (Zn) | 24.2 | 0.045 |
| Cyanide (Cn) | 0.87 | 0.0015 |
| (Source: City and County of San Francisco, 1994 NPDES Permit Program, Attachment #1, Appendix A, page 6) |  |  |

Public notification is required under the draft permit.  This requirement represents a BPT/BCT control for helps to prevent exposure to conventional pollutants (primarily bacteria).

9.	Monitoring to Effectively Characterize CSO Impacts and the Efficacy of CSO Controls:  The City has ongoing shoreline, Ocean, and Bay monitoring programs that include both routine long-term monitoring of overflow and receiving waters and special short-term studies undertaken to support development of CSO control strategies or characterize CSO impacts on beneficial uses.  Shoreline samples are collected for bacteriological analysis three times per week along the San Francisco Bay and Pacific Ocean.  Water and sediment sampling is routinely conducted both in the Bay and Ocean.  Numerous special studies have been conducted since 1966, when the City first undertook an in-depth study of the CSO problem.

Shoreline bacteriological levels have been monitored for the past 15 years at 45 locations around the City at a frequency of 8 to 12 times per month at each site; visual observations of overflow debris and recreational uses in the vicinity of the overflow structures are also reported.  Monitoring results show that coliform levels are elevated at shoreline stations near CSO structures during and shortly after CSO events, but generally return to background levels within one or two tidal cycles following the cessation of the overflow.

Water quality monitoring of overflows has been routinely conducted since 1983, when the City's first CSO control facilities became operational.  Flow-weighted, storm-composite samples are collected using automatic samplers and analyzed for constituents including BOD, TSS, oil and grease, phenols, and metals; in recent years, total PAHs have been added to the routine analysis.  Full-priority pollutant scans are run on representative storm-composite samples of CSO one to two times per year.  As new CSO control facilities come on-line, they will be added to monitoring program.  A special monitoring program in the southeastern portion of the City documents benefits of CSO control on water contact recreation and shellfishing.  Collected data are submitted annually to the Board.

The draft NPDES permit requires continued receiving water monitoring.  This requirement represents both a BCT and BAT control because it helps the City, the Regional Board, and EPA to evaluate the efficacy of the previous controls to remove conventional, toxic and non-conventional pollutants.

II.	BPJ Analysis of Treatment Beyond the Nine Minimum Controls

In Part I of this analysis, EPA has concluded that the nine minimum controls outlined in the Policy are appropriate as minimum BCT/BAT requirements.  In Part II, EPA performs a BPJ analysis on the Westside CSO system in order to determine whether additional technology-based controls should be required in the NPDES permit.  This analysis is also intended to reconsider the issue identified by the Regional Administrator in his Notice of Decision to Repropose Under 40 C.F.R.  124.60(b), dated January 31, 1992:

Whether BAT or BCT requires effluent limitations that reflect the additional amount of pollutant removal achievable through expansion of the [Westside] Transport's existing capacity to  store combined flows for later treatment at the new Oceanside Plant, thus reducing the amount of decant discharged to the SWOO.

A.	Determination of Best Practicable Control Technology Currently Available (BPT) for Combined Sewer Overflows

For many industrial categories, the BPT limitations (as well as BCT and BAT limitations) have been promulgated as regulations (effluent guidelines).  EPA has not formally promulgated technology-based limitations for CSOs and therefore the permit writer must use best professional judgement (BPJ) on a case-by-case basis to develop the appropriate limitations.  The regulations specify the factors to be used by the permit writer (40 CFR 125.3(d)(1)):

(I)	The total cost of application of technology in relation to the effluent reduction benefits to be achieved from such application;

(ii)	The age of equipment and facilities involved;

(ii)	The process employed;

(iv)	The engineering aspects of the application of various types of control techniques;

(v) 	Process changes; and

(vi)	Non-water quality environmental impact (including energy requirements).

The key factor here is item (I), the comparison of costs and performance.  Senator Muskie, one of the authors of the legislation, noted:

The balancing test between total cost and effluent reduction benefits is intended to limit the application of technology only where the additional degree of effluent reduction is wholly out of proportion to the costs of achieving such marginal level of reduction for any class or category of sources.

In other words, Congress expected significant efforts toward pollutant control as a result of the BPT requirements.  Costs for the construction of treatment facilities would be a limiting factor only if they were comparably much higher than experienced by similar industrial sources.  However, very high costs for treatment characterize CSO controls.  The costs of controlling CSOs are very expensive because CSOs are caused by large volumes of highly variable storm runoff which may occur at flow rates much greater than the flow rates of the dry weather sewage.  Additionally, CSO control facilities are only used on an intermittent basis; they are idle most of the year.  As a result of these two factors, costs per pound of pollutant removed for CSO facilities usually greatly exceed the comparable costs for other wastewater pollutant control measures.  This is particularly true in San Francisco where rainfall generally occurs only during a six month period of the year at a rate of approximately 20.5 "/year.

The high costs for CSO control and treatment have resulted in a long-term EPA policy of equating BPT with limited controls not involving significant construction.  Consequently, CSO treatment facilities have been built only when necessary to meet water quality needs.

Application of the Cost Factor to the Determination of BPT for San Francisco:

The determination of BPT requires an examination of the six factors above.  Each of these factors is evaluated below:

(I)	The total cost of application of technology in relation to the effluent reduction benefits to be achieved from such application; (40 CFR 125.3(d)(1))

To determine if the benefits are reasonable compared with costs we can compare San Francisco Westside CSO treatment costs and benefits with sewage treatment plant costs and benefits.  The dry weather pollutants entering sewage treatment plants and the pollutants discharged as CSOs are similar in nature and so a comparison can be made.

Table 2 includes the costs and effluent reductions (benefits) achieved in terms of dollars per pound of suspended solids removed from the wastewater.  Table  2 includes cost data for two Bay area sewage treatment plants and for the San Francisco Westside combined sewer overflow control and treatment facilities.  The two sewage treatment plants treat the wastewater to the secondary level which is the technology-based minimum required by the Clean Water Act.

Table 2

________________________________________________________

Facility				Suspended Solids

(Unit cost for removal)

($/lb)

East Bay MUD*				 $ 0.26

Central Contra Costa S.D.		$  0.51

S.F. Westside CSO control facilities	$ 10.78

_______________________________________________________

Cost Assumptions for S.F. Westside CSO facilities

Tons per year of TSS Removed	676 tons

Required Storage			69 MG

Westside CSO Control Costs		$213,750,000

Expected CSO facility life		50 years

Assumed interest rate		6.5%

Capital Recovery factor		.0679139

Annual Costs

Capital				$14,516,602

O&M (at 0.02 of Cap. Costs)		$42,750

Total				$14,559,352

Cost per pound of TSS removed		$10.78

As shown in the table, based on suspended solids removal, CSO control costs as implemented on San Francisco's Westside are wholly out of proportion to the benefits when compared with comparable costs and benefits at local POTWs.  Consequently, CSO control facilities as built in San Francisco could not be justified based solely on BPT technology-based requirements.  Instead the justification for constructing treatment facilities must be (and was) based on water quality needs.

There are additional methods of evaluating CSO performance. However, suspended solids removal is a practical and useful factor to compare since most pollutants of concern occur as suspended solids and suspended solids by themselves can have detrimental effects.

Though analysis of factor 1 is sufficient to show that the measures employed by San Francisco exceed BPT, this analysis will also examine the other BPT factors:

(ii)	The age of equipment and facilities involved; and (iii) The process employed;

San Francisco began planning for wastewater facilities improvement in 1972, with the preparation of the first Wastewater Master Plan.  Implementation of the Master Plan will be complete in 1996.  The Master Plan evaluated three basic options for wastewater control:  (1) constructing high-capacity wastewater treatment plants, (2) storing excess flows for later treatment, and (3) separating sewers.  The City selected a combination of increased treatment capacity and large volume storage as the most cost-effective means of controlling water quality.  EPA concurred in San Francisco's analysis at the time the Master Plan was developed, and remains convinced that it represents the most cost-effective and environmentally protective strategy for addressing the City's CSO problems.  Sewer separation was rejected because of high costs, the need to excavate every street in the City, and the failure to address pollution caused by stormwater runoff.

On the City's Westside, key facilities are the Oceanside Water Pollution Control Plant (Oceanside WPCP), the Southwest Ocean Outfall (SWOO), and the Westside Storage/Transport facilities.  The Oceanside WPCP came on-line in spring 1994, replacing the Richmond-Sunset treatment plant.  The Oceanside WPCP provides both a higher level of treatment (full secondary treatment) and a larger treatment capacity (total of 65 MGD) than the former treatment facility.  The Westside Storage/Transport facilities capture combined sewage and stormwater runoff and hold as much as possible for later treatment at the Oceanside WPCP.  The SWOO was completed in 1986, and discharges treated wastewater effluent approximately 4.5 miles from shore, and provides effective initial dilution of the effluent.  The Westside Storage/Transport, a 2.5mile long, box-like structure located beneath the Great Highway, is one of the largest wastewater storage structures in the nation.  Storm flows that cannot be stored pass over a weir and under a baffle into a second box, called the decant structure; settleable solids and floatables remain in the first box, and are flushed to the treatment plant after the storm subsides.  Overflow from the decant box passes over another weir and under a baffle, and is routed to the SWOO.  If SWOO's capacity is exceeded, effluent is discharged to the shoreline.  Thus, any combined flows discharged from the storage/transport structures receive primary-equivalent treatment, which removes essentially all macroscopic floatables and most settleable solids.  Once a storm subsides, stored flows are routed to the treatment plant.  Storage/transport structures are subsequently drained to the treatment facilities.

All untreated combined sewage formerly discharged to the shoreline is captured and treated as a result of the Westside construction program.  During rainy weather, approximately 50 percent of the flows are held for treatment at the Oceanside WPCP; the remaining 50 percent receive flow-through treatment within the storage/transport structures.  On average, approximately 87 percent of the combined flows are discharged through the SWOO, and 13 percent are discharged to the shoreline.  These percentages are long-term averages that may not reflect the system's performance for a particular year because of the dynamic nature of the interaction between the system and the characteristics and sequence of storm events.  For example, the system might capture all flows during a relatively intense rainfall of short duration with no overflow, especially when the transport/storage structures are empty at the start of the storm; a storm event of similar intensity and duration, however, might result in an overflow if previous rainfall had partially filled the transports.

| Parameter | Pre-Program | Master Plan | Percent Reduction |
| --- | --- | --- | --- |
| Average Number of Beach Overflows (Range) | 114a (26193) | 8b (118) | 93 |
| Average Annual Volume of Wastewater Discharged, MG (Range) | 2,870 (9265,030) | 449 (151,070) | 84 |
| Average Percentage of Sanitary Flow | 12 | 6.5 | 46 |
| Average Number of Days Recreational Uses Impaired (Range) | 119 (67147) | 25 (651) | 79 |
| Average BOD, lbs/yr x 103 (Range) | 1,220 (3942,140) | 191 (6460) | 84 |
| Average TSS, lbs/yr x 103 (Range) | 12,100 (3,89021,200) | 1,890 (634,550) | 84 |
| (Source: City and County of San Francisco, Revised Overflow Control Study, 1978, plate 8) a. Subsequent to the publication of the 1978 study, the SWRCB changed the definition of an overflow event. Under the current definition, the Westside facilities overflowed an average of 54 times per year. b. Using the present definition of overflow. |  |  |  |

(iv)	The engineering aspects of the application of various types of control techniques;

The range of available CSO control technologies is essentially limited to four core technologies:  storage basins, deep tunnels, swirl concentrators, and screening facilities.  These four technologies fall into two groups.  The first group of CSO control measures, storage basins and deep tunnels, are implemented where receiving water quality impacts are of the greatest concern, and required levels of CSO control are consequently high.  These technologies rely on the storage of excess CSO, with subsequent treatment at existing water pollution control plants, to achieve high pollutant removal rates and effective disinfection levels.  The second group of CSO controls, swirl concentrators and screening facilities, are implemented to reduce settleable solids and floatables.  These technologies are typically applied where receiving water quality conditions do not warrant high BOD/TSS removal.  Sewer separation, a third type of CSO control strategy, is typically used by municipalities that have only a relatively small area served by combined sewers.

Storage BasinsStorage Basins

Storage basins are typically concrete tanks located at overflow points or near treatment plants.  This structurally intensive technology involves the capture and storage of CSOs, with subsequent treatment of captured flows.  Combined flows that exceed the storage capacity of the basin may receive coarse screening, primary settling, floatable removal, and/or disinfection prior to discharge.  Once flow capacity is available at the treatment plant, the stored volume is treated and discharged.  This technology is very flexible because extremely variable CSO flows can be stored and treated, and high removal of BOD and TSS can be achieved.

Deep TunnelsDeep Tunnels

Deep tunnels provide consolidated storage in underground tunnels, from which the CSO is pumped to an existing treatment plant when capacity becomes available.  Pollutant removal effectiveness is limited by the volume of the tunnel; CSO discharges that exceed the storage capacity of the tunnel typically do not receive treatment.  Thus, the CSO that is stored in tunnels can receive a high level of treatment prior to discharge, but flows in excess of the tunnel's capacity typically receive no treatment.

Swirl ConcentratorsSwirl Concentrators

The swirl concentrator is a specially configured gravity solids separator that retains floatables in the unit, passes concentrated solids to the sewer, and discharges the remaining flow to the receiving waterbody.  The swirl concentrator can provide effective separation of floatables over a wide range of hydraulic loadings, while removing approximately 15 percent of suspended solids.

Screening FacilitiesScreening Facilities

Screening of CSOs can be effective in removing large solids and floatables and is typically used in conjunction with other storage and treatment systems.  The effectiveness of this technology is directly related to the size of the screen openings, which can vary from bar racks to coarse and fine screens and microstrainers.  Screened materials are generally removed mechanically.  Screening, a physical treatment process for CSO discharges, is usually applied when a high level of BOD/TSS removal is not necessary.

ConclusionConclusion

Based on this brief review of available CSO control technologies, San Francisco's transport/storage facilities clearly provide the highest level of water quality protection available.  Swirl concentrators and screening facilities can reduce floatables, but provide limited removal of BOD and suspended solids.  Deep tunnels allow for a high level of treatment for combined flows that do not exceed its storage capacity, although combined flows in excess of tunnel capacity receive little or no treatment. In San Francisco's system, combined flows are either stored for later treatment when capacity becomes available at the treatment plant or are subjected to primary-equivalent treatment prior to discharge when transport/storage capacity is exceeded.  This treatment provides the storage benefits of deep tunnels and storage basins, and a high rate of removal for BOD, TSS, floatables, and settleable solids that is not possible with deep tunnels, swirl concentrators, or screening facilities.

(v)	Process changes;

This factor only applies to point source discharges from industrial plants, because industrial plants can consider alterations to processes that affect wastewater quality and quantity.

(vi)	Non-water quality environmental impact (including energy requirements).

See BAT analysis

BPT Summary

The construction of CSO control and treatment facilities cannot be justified based on the application of the BPT cost/benefit criteria to San Francisco's Westside System.  This conclusion is consistent with the long-term policy of both EPA, Region IX and the Regional Water Quality Control Board to base San Francisco's CSO permits (and resultant facility construction) on the need to achieve water quality standards.   BPT does not require any additional measures beyond the six control measures outlined in the 1989 CSO Control Strategy.  NPDES Permit CA0037681 contains effluent limitations that require proper operation of San Francisco's CSO facilities.  Therefore, these effluent limitations ensure that San Francisco will provide treatment in excess of that mandated by BPT requirements.

B.	The Determination of Best Conventional Pollutant Control Technology (BCT) for CSOs.

BCT applies to the following constituents of the combined sewer overflows:  suspended solids, biochemical oxygen demand (BOD), oil & grease, pH, and coliform bacteria.  BCT represents an incremental level of control beyond BPT for the specified pollutants.  The first part of this analysis has shown that the current system surpasses BPT for CSOs.  This portion of the analysis will determine whether the current system also meets BCT or whether additional treatment is necessary.  In addition, EPA's CSO Policy recommends consideration of certain technologies as potential bases for setting BCT effluent limitations.  These are discussed in Section II.

The regulations specify the factors to be used by the permit writer to determine BCT:

(I)	The reasonableness of the relationship between the costs of attaining a reduction in effluent and the effluent reduction benefits derived;

(ii)	The comparison of the cost and level of reduction of such pollutants from the discharge from publicly owned treatment works to the cost and level of reduction of such pollutants from a class or category of industrial sources.

(iii)	The age of equipment and facilities involved;

(iv)	The process employed;

(v)	The engineering aspects of the application of various types of control techniques;

(vi)	Process changes; and

(vii)	Non-water quality environmental impact (including energy requirements).

The determination of BCT requires an examination of the seven factors above.  Each of these factors is evaluated below:

(I)	The reasonableness of the relationship between the costs of attaining a reduction in effluent and the effluent reduction benefits derived;

This portion of the analysis could simply compare the costs of the current  treatment with the effluent reduction benefits derived as done in Table 1 above.    However, since San Francisco built these facilities to meet water quality standards, the question has arisen as to whether any additional treatment could be justified by BCT.  For example, would further conventional pollutant reductions brought about by increased storage (and therefore increased treatment) be incrementally cheap enough to pass the "reasonableness" test?   This analysis therefore compares the most economical additional treatment necessary to further reduce conventionals (i.e. suspended solids) with the cost of the increased treatment:

Analysis of Increased Storage

To further reduce suspended solids, additional storage capacity would have to be added to the current facility.  At a minimum the City estimates that it would cost $2.35 for each additional gallon of storage.  If the portion of decanted wastewater discharged through the SWOO was to first receive treatment at the Oceanside Treatment facility (60% secondary, 40% primary), an additional 69.6 million gallons of storage capacity would be needed.  This facility enhancement would only reduce suspended solids by additional 209 tons per year and would cost approximately $163.6 million or an amortized cost of $11.1 million per year. (Assuming a 50 year project life. 6.5% interest, and a 0.02% of capital costs O&M).  This facility enhancement would thereby cost  approximately $25/lb of TSS removed.  (See Table 4 below).

Analysis of Full Containment

Full containment of storm flow is not required under the CWA's BAT/BCT requirements or by the CSO Control Policy.  In fact, "full containment" of CSOs is extremely difficult to achieve because of the nature of precipitation events and usually defined stochastically (e.g., long-term average of 1, 0.2, or 0.05 overflows to the shoreline per year).  The following section analyzes the costs and environmental benefits of full containment of all Westside storm flows (defined as one overflow per year), which allow for secondary treatment of all combined flows.  Two options that would meet the necessary combination of increased treatment and storage are examined.

Option 1 would provide a limited increase in treatment capacity and a major increase in storage.  This option assumes that the lack of available land or difficulties of constructing satisfactory treatment methods prevent the City from building more than 20 MGD of additional secondary treatment.  Assuming one allowable overflow per year, an additional 515 MG of storage would need to be constructed, over and above an existing 70 MG:  a second storage/transport box under the Great Highway and additional storage/transports under Avenues 45 through 48.  Thirty-foot diameter tunnels would be constructed under Avenues 41 through 44 and part of 40th Avenue; tunnels would be constructed, because the street grade is too high for open-cut construction.  Estimated capital costs for these facilities would be $1.3 billion.

Option 2 assumes that constructing a new 65 MGD secondary treatment plant on the Westside would be possible to double the existing treatment capacity.  In this case, an additional 220 MG of storage would be necessary to provide full secondary treatment to all combined flows, allowing one overflow per year.  Estimated capital cost for this option, not including land acquisition costs for the treatment plant, would be $840 million.

Implementation of one of the above options would reduce TSS loading to the Pacific Ocean by an estimated 420 tons per year, at an incremental removal cost of approximately $68 per pound (Table 4).  The capital cost per City resident would be at least $1,160.

Table 1 shows that the cost of pollutant reduction for San Francisco's present system is exorbitant.  Table 4 shows incremental pollutant reductions which could be gained with increased storage and treatment is even more costly.  Therefore, the costs of both the current facilities and any additional storage or treatment facilities could not be considered "reasonable" when compared to the effluent reduction benefits derived.

| Stage | Annual Cost ($, millions) | Average TSS Discharged (tons/yr) | Average TSS Removeda (tons/yr) | Percent TSS Removala | Increm. Cost of TSS Removal ($/lb)b |
| --- | --- | --- | --- | --- | --- |
| Pre-program Facilitiesc |  | 3,800 |  |  |  |
| Full Master Plan (1996) | 46.5d | 1,580 | 2,220 | 58 | 10.8 |
| Increased Storage Option | 11.1d,g | 1,371 | 2, 429 | 64 | 24.8f |
| Full Secondary on Westside (1 overflow) | 57.2d,e,g | 1,160 | 2,640 | 69 | 68f |
| a Total reductions compared to Pre-Program facilities. b Divides total annual cost by pounds of TSS removed; other measures of water pollutant loading (e.g., BOD and toxic pollutants) also improve. c Pre-program facilities represent the baseline for comparison of TSS emissions. d Assumes a 50-year life, 6.5% interest rate, and O&M of 0.02% of capital cost. e Excludes land acquisition costs for a 65 MGD treatment plant. f For comparison, secondary treatment of wastewater costs approximately $0.26 per pound of TSS removed for the East Bay Municipal Utilities District and approximately $0.51 per pound TSS removal for the Central Contra Costa Sanitation District. g Costs are in addition to those incurred in construction and operation of full master plan. |  |  |  |  |  |

(ii)	The comparison of the cost and level of reduction of such pollutants from the discharge from publicly owned treatment works to the cost and level of reduction of such pollutants from a class or category of industrial sources.

The intent of this factor was summarized in Chemical Manufacturer's Association v. EPA:

Representative Roberts, the author of the conference report on the 1977 amendments, emphasized that the additional technology requirements of BCT were to be imposed only to remove additional "cheap pounds" of conventional pollutants beyond BPT.

Best conventional pollutant control technology (BCT) is intended as an incremental level of control beyond the best practicable control technology currently available (BPT).  The intent of the requirement is to impose additional controls only if the additional removal of conventional pollutants is comparable to removal costs at POTWs.  As shown in Table  2, however, the CSO control technology  implemented by San Francisco is very expensive compared with POTW costs and therefore could not be justified under BCT.   Other  CSO treatment technologies, as listed in Table 5, are far more costly than POTWs, and therefore, also cannot be justified.

| a. The control technology costs in Table are taken from the California Regional Water Quality Control Board BCT/BAT analysis as developed for NPDES CA0037681 (7/26/1990 final permit). The costs were originally developed by East Bay Municipal Utility District. Note that with the exception of sedimentation, these costs for partial treatment are significantly higher than the costs for full-scale CSO control as implemented by San Francisco on the Westside. Control Technology |  | TSS Reduction (percent) | TSS Removal Cost ($/lb) |
| --- | --- | --- | --- |
| CSO Controla | Rotary Screening | 5 | 46 |
|  | Swirl Concentrators | 15 | 21 |
|  | High-Rate Filtration | 20 | 17 |
|  | Sedimentation | 33 | 6 |
| Local POTWsb | East Bay Municipal Utilities District | 85 | 0.26 |
|  | Central Contra Costa County Sanitation Dist. | 85 | 0.51 |
| San Francisco | Westside Facilities | 60 | 10.5 |
| (Source: RWQCB San Francisco Bay Region and the City of San Francisco) |  |  |  |

The TSS Reduction and the corresponding TSS Removal Cost for the CSO Control technologies are calculated assuming that the stormwater/wastewater influent has not undergone any prior treatment.  The TSS percent reduction would be significantly lower and the TSS Removal Cost would be significantly higher if one of these CSO Controls were added to the existing system which already reduces TSS by at least 60%.

b.	POTWs in general have significantly lower treatment costs since they do not treat stormwater.

(iii)	The age of equipment and facilities involved;

See BPT analysis above.

(iv)	The process employed;

See BPT analysis above.

(v)	The engineering aspects of the application of various types of control techniques;

See BPT analysis above.

(vi)	Process changes;

Not Applicable.

(vii)	Non-water quality environmental impact (including energy requirements).

See BAT analysis below.

BCT Summary

Best Conventional Treatment applies to the removal of conventional pollutants (TSS, BOD, etc.).  The viability of a potential BCT treatment is determined by comparing treatment costs with POTW treatment costs.  The costs of  the CSO facilities actually built by San Francisco, the costs of increased storage for later treatment, and the costs for other potential CSO treatment technologies all greatly exceed POTW treatment costs.  Therefore no additional treatment can be justified based solely on  BCT.    NPDES Permit CA0037681 contains effluent limitations that require proper operation San Francisco's CSO facilities.  Therefore, these effluent limitations ensure that San Francisco will provide treatment in excess of that mandated by EPA's BCT requirements.

C.	The Determination of Best Available Technology Economically Achievable (BAT) for CSOs.

BAT requirements are requirements that go beyond BCT by specifying controls for two groups of pollutants:  (1) toxic pollutants (e.g., copper, lead, zinc, polynuclear aromatic hydrocarbons [PAHs], pesticides, and other organics) and (2) non-toxic, non-conventional pollutants.  For CSOs, floatables are the only non-toxic, non-conventional pollutant of concern.  The following CWA regulations for BAT specify factors are used by the permit writer (40 CFR 125.3(d)(3)):

(I)	The age of equipment and facilities involved;

(ii)	The process employed;

(iii)	The engineering aspects of the application of various types of control techniques;

(iv)	Process changes;

(v) 	The cost of achieving such effluent reduction; and

(vi)	Non-water quality environmental impacts (including energy requirements).

Since all wastewater receives at least primary treatment including baffling as it is decanted, San Francisco's system provides substantial treatment for floatables.  EPA has not been able to identify any treatment process that would significantly improve floatables removal, and so finds that baffling constitutes BAT for floatables.

To determine BAT for toxic pollutants (beyond the nine minimum controls discussed in section I), EPA analyzed the existing San Francisco CSO containment and treatment system, and compared it to the regulatory requirements for BAT.  In addition, the Clean Water Act requires EPA to promulgate effluent limitations requiring the elimination of discharges of all pollutants if EPA determines that such elimination is technically and economically achievable.  CWA  301(b)(2)(A).  Therefore, EPA has analyzed the technical and economical achievability of effluent limitations that would effectively eliminate San Francisco's CSO discharge.

The determination of BAT requires an examination of the six factors above.  Each of these factors is evaluated below:

(I)	The age of equipment and facilities involved;

See BPT analysis.

(ii)	The process employed;

See BPT analysis.  The City and County has also implemented a Source Control program which will significantly help to reduce  toxic pollutants discharged by the public and industry.  (See discussion under Section I of this Fact Sheet Amendment,  Control # 7, Pollution Prevention.)

(iii)	The engineering aspects of the application of various types of control techniques;

See BPT analysis

(iv)	Process changes;

Not applicable.  See discussion in BPT analysis.

(v) 	The cost of achieving such effluent reduction;

This item is the key issue.  The high cost of CSO control has prevented many U.S. cities from providing treatment, even when WQSs are being violated.  The City's capital investment for water pollution control has been about $1,900 per person and would be substantially higher in current dollars.  This level of investment represents one of the highest per capita investments for in the nation for a medium or large city.  As noted earlier, this equates to approximately $10.8/lb of TSS removal.  Roughly two thirds of this expense was dedicated to CSO control.

The application of the cost test in the BAT analysis is discussed by the court in NRDC v. EPA, 863 F.2d 1420 (9th Cir. 1988).  The court  concluded:

To demonstrate economic achievability, no formal balancing of costs and benefits is required; BAT should represent "a commitment of the maximum resources economically possible to the ultimate goal of eliminating all polluting discharges."  EPA has considerable discretion in weighing the costs of BAT.... The Administrator should be bound by a test of reasonableness.  NRDC v. EPA, 863 F.2d at 1426 ,(citations omitted).

San Francisco has made an extraordinarily large investment in CSO control technology.  This is consistent with BAT requirements to commit the maximum resources economically possible to the goal of eliminating pollutant discharges.  However, without the associated water quality benefits that justified this investment, EPA would not conclude that this was a reasonable expense to require.  Therefore, EPA concludes that the existing level of storage and treatment for CSOs exceeds BAT requirements for toxic pollutant removals.

This, however, does not conclude EPA's analysis of BAT.  Given the existing treatment system, and the existing resource commitment, EPA has also examined possible mechanisms to improve reductions of toxic pollutants.  This review is appropriate to determine whether it is reasonable to require additional steps to address toxic pollutants when considering the costs already incurred by the program as a whole and the incremental costs and benefits of potential improvements.  Without such a review, cost-effective improvements to toxic pollutant removal could escape consideration simply because so much has been already spent.  The toxic pollutant removal technology examined is increased primary and  secondary treatment of all wastewater and stormwater, as well as toxic pollutant control strategies in EPA's CSO Policy (see Section I).

Analysis of toxic pollutant removal efficiencies through primary and secondary treatment (activated sludge).

For purpose of this cost analysis, additional primary and activated sludge treatment was selected as the most cost efficient toxic removal technology.  This selection is based on a study of 40 POTWs.  The study compares removal efficiencies through primary treatment, activated sludge (secondary), trickling filter, and tertiary treatment.  Copper, Lead, and Zinc were chosen for this analysis.  Removal efficiencies for Copper, Lead, and Zinc are as follows:

Primary	Primary and Secondary

Cu: 	22%		86%

Pb: 	57%		61%

Zn:	27%		79%

Decanting was conservatively estimated to have no effect on metals removal.  (Since decanting does remove some suspended solids, it would likely have some effect on removing metals.  However, no data exists to estimate the amount.)

Site-specific wet-weather influent data for 1994 and 1995 was used. The most cost efficient means to increase the amount of wastewater that receives primary and secondary treatment is to increase storage capacity (as opposed to increasing treatment facilities).

Analysis of Increased Storage

Under this scenario (similar scenario as discussed under BCT above), the 1,280 million gallons per year (MGY) that currently is decanted would receive a combination of primary and secondary (an additional 40 MGY would receive primary and 1,056 (MGY) would receive secondary).  The remaining 184 MGY would  be discharged to the shoreline. (See Table 6).  By multiplying these flows by the removal efficiencies for primary and secondary above, the reductions in loadings were calculated.  Assuming an amortized $11.1 million yearly cost for the additional treatment, the cost/lb of removal was estimated.

Metal          % Reduction                $$/lb removed

Copper		26%			$300

Lead		12%			$1,400

Zinc		21%			$100

Analysis of Full Secondary

By increasing the storage capacity by another 108 Million Gallons, all stormwater/wastewater (except for the eight shoreline overflows) could receive secondary treatment (See Table 6).   While this would further reduce the loadings of metals to the ocean, the cost, of course, would increase significantly. (This scenario is not the same as the "Full Containment" Options discussed under the BCT Analysis.  The scenario is cheaper because is assumes eight overflows per year, and therefore does not require additional treatment facilities.)  The reduction in metals discharged to the ocean was calculated.  Assuming an amortized yearly cost of $28 million, the cost per pound removed was also calculated.

Metal          % Reduction                $$/lb removed

Copper		37%			$500

Lead		12%			$3,700

Zinc		28%			$200

Both the Increased Storage and Full Secondary alternatives would achieve, at best, marginal reductions in toxic pollutant loadings (12% to 37%) at extremely high costs ($100 to $3,700/lb).  These expenditures would be wholly unreasonable given their limited effectiveness.

Table 6: Flow Scenarios for BAT Analysis

| Scenario | Storage Volume (MGY) | Capital Costs for Add. Stor. | Secondary & Primary (MGY) | Primary Only (MGY) | SWOO Decant (MGY) | Shore Decant (MGY) |
| --- | --- | --- | --- | --- | --- | --- |
| Current | 69.4 |  | 8816 | 664 | 1280 | 440 |
| Option 1 | 139 | $164 M | 9872 | 704 | 0 | 624 |
| Option 2 | 247 | $417 M | 10493 | 0 | 0 | 707 |

(vi)	Non-water quality environmental impacts (including energy requirements).

By 1996, the City will have constructed about 70 MG of storage on the Westside, consisting of 47.6 MG in the Westside Storage/Transport project, 19.7 MG in the Richmond and Lake Merced Storage/Transport project, and an additional 2.2 MG of storage in the sewer lines.  The Westside Storage/Transport, one of the largest wastewater storage structures in the nation, is a 2.5-mile long, box-like structure located beneath the Great Highway.  Approaching full containment of combined flows (assuming one overflow per year) would require the construction of either an additional 515 MG of storage or the construction of a 65 MGD wastewater treatment plant and an additional 220 MG of storage.

Constructing the required storage facilities would involve the excavation of many miles of City streets and would be extremely disruptive to local residents.  Constructing an additional wastewater treatment plant in a densely populated city such as San Francisco would be extremely difficult, possibly involving the condemnation of private property.  Neighborhood disruption resulting from construction on this scale would include street closure for up to one year, dust and noise nuisances, potential vibration damage from the excavation and pile-driving equipment, and traffic disruption from truck deliveries and workers commuting to and from construction sites.  Although land and property values would probably be unaffected in the long term, properties in the vicinity of construction activities would likely take longer to sell during the construction period than they would normally.

The fact that these extensive construction activities would occur in a densely populated city and adjacent to environmentally sensitive coastal areas was a consideration for designing and constructing the City's current system to allow for an average of eight overflows per year, rather than one.  In 1979, the SWRCB (with EPA concurrence) granted an exemption to the Ocean Plan that allowed up to eight overflows per year on the Westside, partially due to the fact that the Central Coast Regional Coastal Commission had denied the City a required development permit based on one overflow per year because of the size and location of the transport necessary for a one overflow system.  The major increase in facility size that would be needed was judged to be too disruptive to the coastal area.  Other concerns voiced by the Coastal Commission include future beach erosion, sewer exposure, seismic disturbances, and groundwater problems.

BAT Summary

BAT applies to toxic and non-conventional pollutants.  Based on the guidance provided by the CWA, the costs of increased storage, along with the non-water quality environmental impacts, are excessive compared to the benefits provided, and this  expenditure would be wholly unwarranted under BAT.  The current treatment facilities therefore exceed the cost of treatment facilities that would be required under BAT.

### Attachment 2 – Reasonable Potential Analysis

See Excel Sheet

### Attachment 3 – Memorandum of Agreement

### Please contact Abigail Smith, at ahs@rb2.swrcb.ca.gov for paper copies

Attachment 3 – Memorandum of Agreement

.	City and County of San Francisco.  Westside Operation Plan for the Oceanside Water Pollution Control Plant, January 1990.

.	City and County of San Francisco, 1994 NPDES Permit Program, Attachment 1.  Page 7.

.	City and County of San Francisco, Department of Public Works.  September 1991. Op Cit.

.	San Francisco Public Works Code, Section 118, Article 4.1, Industrial Waste.

.	City and County of San Francisco, Department of Public Works.  Industrial Waste Pretreatment Program Annual Report, June 1992.

.	Ibid.

.	San Francisco Clean Water Program.  Westside Water Pollution Control Facility Planning Report, 1988.  Page 5-5.

.	City and County of San Francisco, Department of Public Works.  Westside Transport Performance Evaluation Study, Final Report, March 1991.

.	James M. Montgomery, Consulting Engineers, Inc.  City and County of San Francisco, Department of Public Works, Best Management Practices Study, August 1992.

.	1972 Leg.Hist. at 170, cited in Chemical Manufacturer's Association v. USEPA, 870 F.2d 177 (5th Cir. 1989)

.	Lam, Johnson, Area Engineer, to John Wolfenden, Section Leader, Internal Memo, BOD and TSS Cost Removal Data or EBMUD and CCCSD, Regional Water Quality Control Board, San Francisco Bay Region, May 19, 1993.

.	City and County of San Francisco,  Department of Public Works, Determination of BCT/BAT for Westside Permits, September 17, 1993, Appendix A.

.	U.S. Environmental Protection Agency.  Cost Estimates for Select Combined Sewer Overflow Control Technologies, 1992.  Page 1.

.	Ibid.  Page 8.

.	EPA Region IX and California Regional Water Quality Control Board.  Fact Sheet, NPDES No. CA 0037681.  Page 12.

?.	City and County of San Francisco, Department of Public Works, Memorandum from Michelle Pla, Planning and Control,  to Shirin Tolle, Environmental Engineer, USEPA, November 12, 1993, pp. 2-4.

.	City and County of San Francisco, September 1991, Op Cit., Page 37.

.	Chemical Manufacturer's Association v. USEPA, 870 F.2d 177 (5th Cir. 1989), p. 205 citing Rep. Roberts in 1977 Leg.Hist. at 330.

.	EPA Guidance Manual on the Development and Implementation of Local Discharge Limitations Under the Pretreatment Program, December 1987, pp.3-55 - 3-58.

.	EPA Region 9, Memo to files from Doug Liden, Engineer, "Calculations of Metals Removal Achievable Through Additional Storage," June 1, 1995.

.	Ibid.

.		City and County of San Francisco.  Control of Westside Storm Flows, September 1991.  Page 31.

.		California Water Resources Control Board.  Order No. WQ 79-16.  Page 15.

?	CSO is defined under Section I.A. of EPAs 1994 CSO Control Policy as  the discharge from a combined sewer system (CSS) at a point prior to the Publicly Owned Treatment Works (POTW)  treatment plant.  A CSS is defined as  A wastewater collection system owned by a State or municipality which conveys sanitary wastewater (domestic, commercial, and industrial wastewater) and storm water through a single pipe system to a POTW treatment plant.