## Eff Conc.
Effluent Concentrations (mg/l)
Month | Sample Date | Flow (MGD) | TDN (mg/L) | Qualifier for TKN | TKN (mg/L) | Qualifier for SKN | SKN (mg/L) | Qualifier for NO3 | Nitrate (NO3) (mg/L) | Qualifier for NO2 | Nitrite (NO2) (mg/L) | Qualifier for Total Ammonia | Total Ammonia (mg/L) | Qualifier for Total P | Total P (mg/L) | Qualifier for Total P (S) | Total P(S) (mg/L) | Qualifier for Diss. Ortho P | Diss. Ortho P (mg/L) | Qualifier for Total Ortho P | Total Ortho P (mg/L) | pH (Standard Units) |  |  | Temperature (deg. Celcius) |  |  | Qualifier for TSS | TSS (mg/L)
|  | Ave Daily | H+J+L | (<, J, or DNQ) |  | (<, J, or DNQ) |  | (<, J, or DNQ) |  | (<, J, or DNQ) |  | (<, J, or DNQ) |  | (<, J, or DNQ) |  | (<, J, or DNQ) |  | (<, J, or DNQ) | Grab | (<, J, or DNQ) | Grab | Min | Max | Ave | Min | Max | Ave | (<, J, or DNQ)
2012-07-01 | 2012-07-06 | 6.78 | 8.36 |  | 1.8 |  | 2 |  | 6.1 |  | 0.26 |  | 0.51 |  | 0.15 |  | 0.18 | J, DNQ | 0.015 | J, DNQ | 0.031 | 7.4 | 7.81 | 7.66 | 28.6 | 33 | 30.6 |  | 3.2 | Note: The 3rd party analytical laboratory errantly ran the grab sample for nitrite instead of the composite sample. By the time this was identified, the composite sample was past the hold time.
2012-08-01 | 2012-08-09 | 6.29 | 5.636 |  | 5.2 |  | 4.8 |  | 0.77 |  | 0.066 |  | 3.1 |  | 0.13 |  | 0.11 |  |  |  |  | 7.23 | 7.8 | 7.61 | 28 | 33.3 | 30.5 |  | 3.1
2012-08-01 | 2012-08-16 | 6.51 | [15 empty] | < | 0.006 | J, DNQ | 0.008 | 7.4 | 7.86 | 7.7 | 26.5 | 31.2 | 28.7
2012-09-01 | 2012-09-12 | 5.23 | 4.672 |  | 3 |  | 2.8 |  | 1.8 |  | 0.072 |  | 2 | J, DNQ | 0.082 | J, DNQ | 0.053 | < | 0.006 |  | 0.01 | 7.21 | 7.62 | 7.47 | 24.5 | 30 | 26.8 |  | 2.9
2012-10-01 | 2012-10-12 | 3.25 | 6.54 |  | 6.5 |  | 6.4 | J, DNQ | 0.083 |  | 0.057 |  | 5.4 |  | 0.22 |  | 0.085 |  |  |  |  | 7.17 | 8.11 | 7.43 | 16.4 | 23 | 20.7 |  | 10.5 | Quarterly report due by 30 Oct.
2012-10-01 | 2012-10-13 | 4.84 | [16 empty] | 0.021 |  | 0.075 | 7.04 | 7.27 | 7.14 | 22.6 | 24.4 | 23.3
2012-11-01 | 2012-11-16 | 7.2 | 8.15 |  | 3.4 |  | 2.9 |  | 4.8 |  | 0.45 |  | 1.5 |  | 0.16 | J, DNQ | 0.072 | < | 0.006 |  | 0.14 | 7.08 | 7.25 | 7.18 | 23.9 | 26.2 | 24.9 |  | 14
2012-12-01 | 2012-12-14 | 7.26 | 5.7 |  | 3.8 |  | 3.5 |  | 1.7 |  | 0.5 |  | 2.7 |  | 0.17 |  | 0.041 |  | 0.02 |  | 0.028 | 6.9 | 7.53 | 7.29 | 20.4 | 23.2 | 21.4 |  | 15.1 | Note: TSS data from 12/7/2012 is used here.
2013-01-01 |  |  | 0 | [26 empty] | Quarterly report due by 30 Jan.
2013-02-01 |  |  | 0
2013-03-01 |  |  | 0
2013-04-01 |  |  | 0 | [26 empty] | Quarterly report due by 30 Apr.
2013-05-01 |  |  | 0
2013-06-01 |  |  | 0
2013-07-01 |  |  | 0 | [26 empty] | Interim report due by 31 July
2013-08-01 |  |  | 0
2013-09-01 |  |  | 0
2013-10-01 |  |  | 0 | [26 empty] | Quarterly report due by 30 Oct.
2013-11-01 |  |  | 0
2013-12-01 |  |  | 0
2014-01-01 |  |  | 0 | [26 empty] | Quarterly report due by 30 Jan.
2014-02-01 |  |  | 0
2014-03-01 |  |  | 0
2014-04-01 |  |  | 0 | [26 empty] | Quarterly report due by 30 Apr.
2014-05-01 |  |  | 0
2014-06-01 |  |  | 0 | [26 empty] | Final report due by 31 July - End of 13267 requirement
Effluent Concentrations (mg/l)
Two additional samples during peak flow each wet season (November thru April)
Wet 2012/3 | 2012-12-05 | 8.91 | 4.47 |  | 3.9 |  | 2.9 |  | 1.2 |  | 0.37 |  | 2.1 |  | 0.28 |  | 0.1 | J,DNQ | 0.015 |  | 0.11 | 7.29 | 7.48 | 7.41 | 22.4 | 24.3 | 23.7
| 2012-12-07 | 5.5 | [19 empty] | 7.23 | 7.59 | 7.48 | 22.1 | 24.1 | 23.2 |  | 15.1
Wet 2012/3 |  |  | 0
Wet 2013/4 |  |  | 0
Wet 2013/4 |  |  | 0
Note on L6: Michael.Armour: Grab sample - see note in column AE
Note on T6: Michael.Armour: Result J-Flagged
Note on V6: Michael.Armour: Result J-Flagged
Note on T8: Michael.Armour: Result was ND; MDL was 0.006 mg/l; Calculation is based on the MDL value
Note on V8: Michael.Armour: Result was J-flagged
Note on P9: Michael.Armour: Result J-Flagged
Note on R9: Michael.Armour: Result J-flagged
Note on T9: Michael.Armour: Result was ND; MDL was 0.006 mg/l; Calculation is based on the MDL value
Note on AD13: Michael.Armour: Uses data from 12.7.2012

## Eff Loads
Effluent Loads (Kg/d) [mg/l X MGD X 3.78 = Kg/d]
Date | Flow (MGD) | TDN | TKN | SKN | Nitrate (NO3) | Nitrite (NO2) | Total Ammonia | TP | TP(S) | Diss. Ortho P | Total Ortho | TSS
Ave Daily
2012-07-06 | 6.78 | 214.2534 | 46.1311 | 51.2568 | 156.3332 | 6.6634 | 13.0705 | 3.8443 | 4.6131 | 0.38443 | 0.79448 | 82.0109
2012-08-09 | 6.29 | 134.0027 | 123.6362 | 114.1258 | 18.3077 | 1.5692 | 73.7062 | 3.0909 | 2.6154 | 0 | 0 | 73.7062
2012-08-16 | 6.51 | [8 empty] | 0.14765 | 0.19686
2012-09-12 | 5.23 | 92.3626 | 59.3082 | 55.3543 | 35.5849 | 1.4234 | 39.5388 | 1.6211 | 1.0478 | 0.11862 | 0.19769 | 57.3313
2012-10-12 | 3.25 | 80.3439 | 79.8525 | 78.624 | 1.0197 | 0.70025 | 66.339 | 2.7027 | 1.0442 | 0 | 0 | 128.9925 | Quarterly report due by 30 Oct.
2012-10-13 | 4.84 | [8 empty] | 0.3842 | 1.3721
2012-11-16 | 7.2 | 221.8104 | 92.5344 | 78.9264 | 130.6368 | 12.2472 | 40.824 | 4.3546 | 1.9596 | 0.1633 | 3.8102 | 381.024
2012-12-14 | 7.26 | 156.424 | 104.2826 | 96.0498 | 46.6528 | 13.7214 | 74.0956 | 4.6653 | 1.1252 | 0.54886 | 0.7684 | 414.3863
2013-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quarterly report due by 30 Jan.
2013-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-03-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quarterly report due by 30 Apr.
2013-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quarterly report due by 31 July
2013-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-09-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-10-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quarterly report due by 30 Oct.
2013-11-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quarterly report due by 30 Jan.
2014-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-03-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quarterly report due by 30 Apr.
2014-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2014-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Quarterly report due by 30 July - End of 13267 requirement
Effluent Loads (kg/d)
Two additional samples during peak flow each wet season
2012-12-05 | 8.91 | 150.5487 | 131.3512 | 97.6714 | 40.4158 | 12.4615 | 70.7276 | 9.4303 | 3.368 | 0.5052 | 3.7048
2012-12-07 | 5.5 | [10 empty] | 313.929
Wet 2012/3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wet 2013/4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wet 2013/4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on K8: Michael.Armour: Analytical result was ND with an MDL of 0.006 mg/l; Calculation is based on the MDL value
Note on K9: Michael.Armour: Analytical result was ND with an MDL of 0.006 mg/l; Calculation is based on the MDL value

## Eff QAQC MLs
Effluent MDL / ML (mg/l)
(1/month)
Date | TKN |  |  | SKN |  |  | NO3 |  |  | NO2 |  |  | Total NH3 |  |  | TP |  |  | TP(S) |  |  | Diss OrthoP |  |  | Total OrthoP |  |  | TSS
(mm/dd/yyyy) | Method | MDL | ML(*) | Method | MDL | ML(*) | Method | MDL | ML(*) | Method | MDL | ML(*) | Method | MDL | ML(*) | Method | MDL | ML(*) | Method | MDL | ML(*) | Method | MDL | ML(*) | Method | MDL | ML(*) | Method | MDL | ML(*)
2012-07-06 | SM20 4500-NH3 C | 0.07 | 0.1 | SM20 4500-NH3 C | 0.07 | 0.1 | EPA 353.2 | 0.1 | 0.2 | SM20 4500-NO2 B | 0.002 | 0.03 | SM20 4500-NH3 C | 0.04 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.006 | 0.1 | SM20 4500-P E | 0.006 | 0.1 | SM 2540-D | 2 | n/a
2012-08-09 | SM20 4500-NH3 C | 0.07 | 0.1 | SM20 4500-NH3 C | 0.07 | 0.1 | EPA 353.2 | 0.1 | 0.02 | SM20 4500-NO2 B | 0.002 | 0.03 | SM20 4500-NH3 C | 0.04 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | [6 empty] | SM 2540-D | 2 | n/a
2012-08-16 | [21 empty] | SM20 4500-P E | 0.006 | 0.1 | SM20 4500-P E | 0.006 | 0.1
2012-09-12 | SM20 4500-NH3 C | 0.07 | 0.1 | SM20 4500-NH3 C | 0.07 | 0.1 | EPA 353.2 | 0.1 | 0.02 | SM20 4500-NO2 B | 0.002 | 0.03 | SM20 4500-NH3 C | 0.04 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.006 | 0.1 | SM20 4500-P E | 0.006 | 0.1 | SM 2540-D | 2 | n/a | Quarterly report due by 30 Oct.
2012-10-12 | SM20 4500-NH3 C | 0.07 | 0.1 | SM20 4500-NH3 C | 0.07 | 0.1 | EPA 353.2 | 0.1 | 0.02 | SM20 4500-NO2 B | 0.002 | 0.03 | SM20 4500-NH3 C | 0.04 | 0.1 | SM20 4500-P E | 0.007 | 0.01 | SM20 4500-P E | 0.007 | 0.01 | [6 empty] | SM 2540-D | 2 | n/a
2012-10-13 | [21 empty] | SM20 4500-P E | 0.006 | 0.01 | SM20 4500-P E | 0.006 | 0.01
2012-11-16 | SM20 4500-NH3 C | 0.07 | 0.1 | SM20 4500-NH3 C | 0.07 | 0.1 | EPA 353.2 | 0.1 | 0.2 | SM20 4500-NO2 B | 0.002 | 0.03 | SM20 4500-NH3 C | 0.04 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.006 | 0.1 | SM20 4500-P E | 0.006 | 0.1 | SM 2540-D | 2 | n/a
2012-12-14 | SM20 4500-NH3 C | 0.07 | 0.1 | SM20 4500-NH3 C | 0.07 | 0.1 | EPA 353.2 | 0.1 | 0.02 | SM20 4500-NO2 B | 0.002 | 0.03 | SM20 4500-NH3 C | 0.04 | 0.1 | SM20 4500-P E | 0.01 | 0.007 | SM20 4500-P E | 0.01 | 0.007 | SM20 4500-P E | 0.006 | 0.01 | SM20 4500-P E | 0.006 | 0.01 |  |  |  | Quarterly report due by 30 Jan.
2013-01-01
2013-02-01
2013-03-01 | [30 empty] | Quarterly report due by 30 Apr.
2013-04-01
2013-05-01
2013-06-01 | [30 empty] | Quarterly report due by 30 July - End of 13267 requirement for minor dischargers
2013-07-01
2013-08-01
2013-09-01 | [30 empty] | Quarterly report due by 30 Oct.
2013-10-01
2013-11-01
2013-12-01 | [30 empty] | Quarterly report due by 30 Jan.
2014-01-01
2014-02-01
2014-03-01 | [30 empty] | Quarterly report due by 30 Apr.
2014-04-01
2014-05-01
2014-06-01 | [30 empty] | Quarterly report due by 30 July - End of 13267 requirement for major dischargers
Wet 2012/3 (12/5/2012) | SM20 4500-NH3 C | 0.07 | 0.1 | SM20 4500-NH3 C | 0.14 | 0.2 | EPA 353.2 | 0.1 | 0.02 | SM20 4500-NO2 B | 0.004 | 0.06 | SM20 4500-NH3 C | 0.04 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.015 | 0.1 | SM20 4500-P E | 0.006 | 0.1 | SM20 4500-P E | 0.006 | 0.1
Wet 2012/3 (12/7/2012) | [27 empty] | SM 2540-D | 2 | n/a
Wet 2012/3
Wet 2013/4
Wet 2013/4
*As noted in Shell's sampling plan, Shell interprests “minimum level” to mean “minimum reporting level”.