## Sheet1
EArticle | ESection No. | ESubdivision | ELanguage | NArticle | NSection No. | NSubdivision | NLanguage
1 | 2611 | (0) | Additional Definitions | 1 | 2611 |  | Additional Definitions
| 2611 | (0) | Unless the context requires otherwise, the following definitions shall apply to terms used in this chapter: | 1 | 2611 |  | Unless the context requires otherwise, the following definitions shall apply to terms used in this chapter:
|  |  |  | 1 | 2611 | "Abandoned underground storage tank" | "Abandoned underground storage tank” means an underground storage tank that: (a) Has not had a functional release detection system for more than 365 days; (b) Does not have a current operating permit; (c) Has not been permanently or temporarily closed in accordance with article 8; and (d) Is not a decommissioned tank.
|  |  |  | 1 | 2611 | "Abatement" | “Abatement” means any activity necessary to reduce, control, or eliminate the effects of an unauthorized release, including, but not limited to, corrective action. Abatement does not include any of the following activities. (a) Implementation of soil, groundwater, or stormwater management or mitigation plans associated with property redevelopment construction or grading activities at a site where an underground storage tank case has received a uniform closure letter pursuant to section 25296.10 of the Health and Safety Code; (b) Detection, confirmation, or reporting of the unauthorized release; or (c) Repairing, upgrading, replacing, or removing an underground storage tank.
|  |  |  | 1 | 2611 | "ASTM A53" | “ASTM A53” means the 2024 American Society of Testing and Materials International standard A53, hereby incorporated by reference.
|  |  |  | 1 | 2611 | "Buried" | "Buried" means covered in earthen material or otherwise concealed from visual observation. For emergency tank systems, “buried” does not include piping in a conduit through building walls or ceilings where both sides of the penetration can be visually observed.
|  |  |  | 1 | 2611 | "Clean compactable backfill" | “Clean compactable backfill” means compactable material used to backfill an excavation for removal of an underground storage tank that is free of vegetation, organic matter, pollutants, and debris that can be used to create a firm, stable foundation.
1 | 2611 | Connected piping | "Connected piping" means all underground piping including valves, elbows, joints, flanges, and flexible connectors attached to a tank system through which hazardous substances flow. For the purpose of determining how much piping is connected to any individual underground storage tank system, the piping that joins two underground storage tank systems should be allocated equally between them. | 1 | 2611 | "Connected piping" | “Connected piping” means all underground, unless specifically excluded or exempted in chapter 6.7 of division 20 of the Health and Safety Code or this chapter: (a) All piping attached to a Type 1 underground storage tank, through which hazardous substances may flow, including valves, elbows, joints, flanges, and flexible connectors attached to a tank system through which hazardous substances flow. (b) All piping attached to a Type 2 or Type 3 underground storage tank, through which hazardous substances may flow, including valves, elbows, joints, flanges, and flexible connectors, and those portions of vent lines, vapor recovery lines, and fill pipes that are beneath the surface of the ground. (c) For the purpose of determining how much piping is connected to any individual underground storage tank system, the All piping that joins two underground storage tanks systems should be allocated equally between them. (d) All piping that connects an underground storage tank to a tank in an underground area should be allocated as specified in section 2612(l).
|  |  |  | 1 | 2611 | "Emergency tank system" | “Emergency tank system” means an underground storage tank system that stores diesel fuel or kerosene solely for use during emergencies by one or more of the stationary devices in accordance with section 25281.5(c) of the Health and Safety Code.
1 | 2611 | Free product | “Free product” refers to a hazardous substance that is present as a non-aqueous phase liquid (e.g., liquid not dissolved in water). | 1 | 2611 | "Free product" | “Free product” refers to means a hazardous substance that is present as a non-aqueous phase liquid (i.e.g., liquid not dissolved in water).
1 | 2611 | Ground water | “Ground water” means subsurface water which will flow into a well. | 1 | 2611 | "Groundwater" | "Ground water" means subsurface all water which will flow into a well beneath the surface of the Earth within the zone below the water table in which the soil is completely saturated with water, but does not include water that flows in known and definite channels.
1 | 2611 | Integral secondary containment | “Integral secondary containment” means a secondary containment system manufactured as part of the underground storage tank. | 1 | 2611 | "Integral secondary containment" | “Integral secondary containment” means a secondary containment system manufactured as part of the underground storage tank.
1 | 2611 | Tank integrity test | “Tank integrity test” means a test method that can ascertain the physical integrity of any underground storage tank. The term includes only test methods which are able to detect a leak of 0.1 gallons per hour with a probability of detection of at least 95 percent and a probability of false alarm of five percent or less. The test method may be either volumetric or non-volumetric in nature. A leak rate is reported using a volumetric test method, whereas, a non-volumetric test method reports whether a substance or physical phenomenon is detected which may indicate the presence of a leak. | 1 | 2611 | "Tank iIntegrity test" | “Tank iIntegrity test” means a volumetric or nonvolumetric test method that can used to ascertain the physical integrity of any underground storage tank or connected piping. The term "integrity test" includes only those test methods which are able to that can detect a leak release of 0.1 gallon per hour for Type 1 underground storage tanks and 0.005 gallon per hour for Type 2 and Type 3 underground storage tanks, with a probability of detection of at least 95 percent and a probability of false alarm of five percent or less. The test method may be either volumetric or non-volumetric in nature. A leak rate is reported using a volumetric test method, whereas, a non-volumetric test method reports whether a substance or physical phenomenon is detected which may indicate the presence of a leak.
1 | 2611 | Interstitial space | “Interstitial space” means the space between the primary and secondary containment systems. | 1 | 2611 | "Interstitial space" | “Interstitial space” means the space between the primary and secondary containment systems.
|  |  |  | 1 | 2611 | "Programming" | "Programming" means the coded instructions for release detection equipment or electronic overfill prevention equipment.
10.5 | 2717 | (a) | “Significant Violation” means the failure of a person to comply with any requirement of Chapter 6.7 of the Health and Safety Code or any regulation adopted pursuant to Chapter 6.7, not including the corrective action requirements in Section 25296.10 of the Health and Safety Code and Article 11 of Chapter 16 of Title 23 of the regulations, that is any of the following: (1) A violation that is causing, or threatens to cause a liquid release of petroleum from an underground storage tank system, including, but not limited to: the failure of any required overfill prevention system, where the failure is causing or threatens to cause a release; or the failure of a required spill containment structure, where the failure is causing or threatens to cause a release to the environment due to a spill or an overfill. (2) A violation that impairs the ability of an underground storage tank system to detect a liquid leak or contain a liquid release of petroleum in the manner required by law, including, but not limited to: tampering with leak detection equipment so that the equipment is no longer capable of detecting a leak at the earliest possible opportunity. (3) A chronic violation or a violation that is committed by a recalcitrant violator. In determining whether a violation is chronic or a violator is recalcitrant, the local agency shall consider whether there is evidence indicating that the violator has engaged in a pattern of neglect or disregard with respect to any requirement of Chapter 6.7 or of any regulation adopted pursuant to Chapter 6.7, not including the corrective action requirements in Section 25296.10 of the Health and Safety Code and Article 11 of Chapter 16 of Title 23 of the regulations. | 1 | 2611 | "Significant violation" | “Significant violation” means the failure of a person to comply with a violation, or a combination of violations, of any requirements of chapter 6.7 of division 20 of the Health and Safety Code, or any regulation adopted pursuant to Chapter 6.7 this chapter, not including the corrective action requirements in section 25296.10 of the Health and Safety Code and article 10, 11 of Chapter 16 of Title 23 of the regulations, that is any of that meets one of the following: (1a) A violation, or a combination of violations, that is causing, or threatens to cause a liquid an unauthorized release of petroleum a hazardous substance from an underground storage tank system, including, but not limited to, the failure of any part of the release detection system, required overfill prevention system, spill containment system, or any other release detection or prevention system where the failure is causing or threatens to cause a release; or the failure of a required spill containment structure, where the failure is causing or threatens to cause a release to the environment due to a spill or an overfill.; (2b) A violation, or combination of violations, that impairs the ability of an underground storage tank system to detect a liquid leak release at the earliest possible opportunity or contain a liquid release of petroleum hazardous substance in the manner required by law, including, but not limited to:, tampering with leak release detection equipment so that the equipment is no longer capable of detecting a leak release at the earliest possible opportunity.; (3c) A class II violation, or a combination of violations, that is chronic violation that is or committed by a recalcitrant violator. In determining whether a violation is chronic or a violator is recalcitrant, tThe local agency Unified Program Agency, or the Board in consultation with the Unified Program Agency, shall must consider whether there is evidence indicating that the violator has engaged in a pattern of neglect or disregard with respect to any requirement of Chapter 6.7 or of any regulation adopted pursuant to Chapter 6.7, not including the corrective action requirements in Section 25296.10 of the Health and Safety Code and Article 11 of Chapter 16 of Title 23 of the regulations previous Class II violation or order; and (d) A violation that causes any underground storage tank not to meet the construction requirements of section 25290.1, 25290.2, or paragraphs (1) through (6) of section 25291(a) of the Health and Safety Code.
1 | 2611 | Under-dispenser containment | “Under-dispenser containment” means secondary containment that is located under a dispenser. | 1 | 2611 | "Under-dispenser containment" | “Under-dispenser containment” means secondary a containment sump that is located under a dispenser that is designed to contain an unauthorized release from the dispenser and prevents the unauthorized release from entering the soil or waters of the State.
|  |  |  | 1 | 2611 | "Vapor condensate trap" or "vapor pot" | “Vapor condensate trap” or “vapor pot” means a small primary containment vessel designed to accumulate condensed vapors from underground storage tank vent and vapor recovery piping when it is not possible to achieve the necessary slope from the dispenser or vent location to the tank. The terms “vapor condensate trap” or “vapor pot” include condensate pots, liquid condensate traps, and knock-out ports.
|  |  |  | 1 | 2611 | "Violation classification" | “Violation classification” means the classification of violations of requirements of chapter 6.7 of division 20 of the Health and Safety Code, or this chapter, not including the corrective action requirements in section 25296.10 of the Health and Safety Code and article 10, as class I violations, class II violations, or minor violations. Class I violation, class II violation, and minor violation are defined as follows: (a) “Class I violation” means a violation that is a significant violation. (b) “Class II violation” means any of the following: (1) A violation, or combination of violations, for the failure to conduct or pass a test; (2) A release detection violation, or combination of release detection violations, that does not meet the criteria for a class I violation; and (3) A minor violation, or a combination of minor violations, that is chronic or is committed by a recalcitrant violator. In determining whether a violation is chronic, or a violator is recalcitrant, the Unified Program Agency, or the Board in consultation with the Unified Program Agency, must consider whether the violator has engaged in a pattern of neglect or disregard with respect to applicable regulatory requirements. (c) “Minor violation” means a violation, or combination of violations, that does not meet the criteria for either a class I violation or a class II violation.
11 | 2720 | (0) | Additional Definitions | 1 | 2611 |  | Additional Definitions
2 | 2620 | (0) | Exemptions to the Regulations | 1 | 2612 |  | Exclusions and Exemptions to the Regulations from this Chapter
2 | 2620 | (a)(5) | A liquid asphalt tank. | 1 | 2612 | (b) | A liquid asphalt tank containing steam-refined asphalt that is not liquid at standard temperature and pressure, which means at 60 degrees Fahrenheit and 14.7 pounds per square inch absolute.
2 | 2620 | (a)(13) | Drums located in basements and which contain 55 gallons or less of a hazardous substance. | 1 | 2612 | (i) | Drums A drum, or other portable container, located in a basements or other below-grade structure, and which that contains 55 gallons or less of a hazardous substance.
|  |  |  | 1 | 2612 | (l) | A tank in an underground area which meets the requirements of section 25270.2(o) of the Health and Safety Code. For purposes of this chapter, other than containment sumps attached to an underground storage tank, a tank in an underground area includes any portion of petroleum supply or return piping extending beyond the underground storage tank’s tank top fittings, including associated pumps and components, dedicated solely to connecting the underground storage tank to one or more tanks in an underground area.
2 | 2620 | (a)(9) | A pipeline located in a refinery or in an oil field unless the pipeline is connected to an underground storage tank. | 1 | 2612 | (m) | A pipeline located in a refinery or in an oil field unless the pipeline is connected to an underground storage tank.
|  |  |  | 1 | 2612 | (n) | Unburied fuel delivery piping at marinas if the owner or operator conducts daily visual inspections of the piping and maintains a log of inspection results for review by the Unified Program Agency.
|  |  |  | 1 | 2612 | (o) | Unburied fuel piping connected to an emergency tank system if the owner or operator conducts visual inspections of the hazardous substance primary containment piping each time the tank system is operated, but no less than monthly, and maintains a log of inspection results for review by the Unified Program Agency.
2 | 2620 | (a)(1) | A farm tank. | 1 | 2612 | (p) | A tank or combination of manifolded tanks located on a farm tank that holds no more than 1,100 gallons of petroleum which is used for fueling motor vehicles used primarily for agricultural purposes and is not for resale.
2 | 2620 | (a)(2) | A heating oil tank. | 1 | 2612 | (q) | A tank located on a farm or at a personal residence that holds no more than 1,100 gallons of home heating oil tank solely for consumptive use at the premises where the tank is located.
2 | 2620 | (a)(3) | A hydraulic lift tank in accordance with section 25281(y) of the Health and Safety Code. | 1 | 2612 | (r) | A hydraulic lift tank in accordance with section 25281(y) of the Health and Safety Code containing hydraulic fluid for a closed loop mechanical system that uses compressed air or hydraulic fluid to operate lifts, elevators, and other similar devices.
|  |  |  | 1 | 2612 | (s) | Underground storage tanks that are part of an emergency generator system at nuclear power generator facilities licensed by the Nuclear Regulatory Commission pursuant to 10 CFR Part 50 Appendix A.
2 | 2620 | (a)(16) | Any structure specifically exempted by section 25281(y) of the Health and Safety Code. | 1 | 2612 | (t) | Any other tank or structure not listed above that is excluded from the definition of an “underground storage tank” in section 25281 of the Health and Safety Code or specifically exempted by section 25281(y) of from the requirements of this chapter pursuant to the Health and Safety Code.
|  |  |  | 1 | 2613 |  | Recordkeeping
|  |  |  | 1 | 2613 | (a) | The owner or operator must submit all the following to the Unified Program Agency:
|  |  |  | 1 | 2613 | (a)(03) | UST Monitoring Plan;
|  |  |  | 1 | 2613 | (a)(08) | Designated UST Operator Identification;
10 | 2712 | (b) | The owner or operator shall maintain the following records on-site, or off-site at a readily accessible location if approved by the local agency, for the specified period. These records shall be made available, upon request within 36 hours, to the local agency or the State Water Board. | 1 | 2613 | (c) | The owner or operator shall must maintain the following records on- site, or off- site at a readily accessible location if approved by the local agency Unified Program Agency, for the specified period. no less than 36 months: These records shall be made available, upon request within 36 hours, to the local agency or the State Water Board.
|  |  |  | 1 | 2613 | (c)(03) | Spill Containment Testing Report Forms and attachments;
10 | 2712 | (b)(3) | Records pertaining to a cathodic protection system shall be maintained for at least 78 months; | 1 | 2613 | (d) | Records pertaining to a The owner or operator must maintain cathodic protection system shall be maintained test results on site, or off site at a readily accessible location if approved by the Unified Program Agency, for at least no less than 78 months.
|  |  |  | 1 | 2613 | (e) | The following records must be maintained by the owner or operator on site, or off site at a readily accessible location if approved by the Unified Program Agency, for the life of the underground storage tank system:
|  |  |  | 1 | 2613 | (f) | Maintaining documents electronically, so that they are readily accessible on site through electronic means during inspections satisfies a requirement to maintain the records on site.
|  |  |  | 1 | 2613 | (g) | The Unified Program Agency may approve an owner or operator maintaining documents off site at a readily accessible location. The Unified Program Agency must document the approval and any conditions of the approval.
|  |  |  | 1 | 2613 | (h) | Documents maintained off site must be provided within 36 hours of being requested by the Unified Program Agency, the Board, a special inspector, or an independent compliance inspector.
|  |  |  | 1 | 2614 |  | Test Notification
|  |  |  | 1 | 2614 |  | The underground storage tank owner or operator must notify the Unified Program Agency in writing at least 72 hours prior to conducting a test of underground storage tank components or systems unless the notification requirement is waived by the Unified Program Agency.
8 | 0 | (0) | Site Specific Variance Procedures | 2 | 0 |  | Site-Specific Variance Procedures and Additional Construction Standards
8 | 2681 | (0) | Site Specific Variances | 2 | 2620 |  | Site-Specific Variances
8 | 2681 | (a) | A site-specific variance allows an alternative method of construction or monitoring which would be applicable at one or more sites within a local agency's jurisdiction. Application for a site-specific variance shall be made to the appropriate Regional Water Quality Board. | 2 | 2620 | (a) | A site-specific variance allows an alternative construction or release detection method of construction or monitoring which would be applicable at one or more sites within a local agency's Unified Program Agency's jurisdiction. Application for a site-specific variance shall be made to the appropriate Regional Water Quality Board. A site-specific variance only is available before the installation of alternate components. The site-specific variance, if approved, would apply only to the specific site(s) approved for a variance.
8 | 2681 | (b) | Prior to applying to the Regional Water Quality Board for a variance, the applicant shall submit a complete construction and monitoring plan to the local agency. The proposed alternative construction or monitoring methods which may require a variance shall be clearly identified. If the local agency decides that a variance would be necessary to approve the specific methods or if the local agency does not act within 60 calendar days of receipt of a complete construction and monitoring plan from the applicant, the applicant may submit the variance application to the Regional Water Quality Board. | 2 | 2620 | (b) | Prior to commencement of underground storage tank system installation and applying to the Regional Water Quality Board for a variance, the applicant shall submit person must provide a complete construction plans and a proposed monitoring plan to the locsl agency Unified Program Agency. The proposed alternative construction or monitoring release detection methods and equipment which may require a variance shall must be clearly identified. If the local agency Unified Program Agency decides that a variance would be necessary to approve the specific methods or if the Unified Program Agency does not act within 60 calendar days of receipt of a complete construction and monitoring plan from the applicant person, the applicant person may submit the a variance application to the Regional Water Quality Board with a copy to the Board.
8 | 2681 | (c) | An application for a site-specific variance shall include, but is not limited to: | 2 | 2620 | (c) | An application for a site-specific variance shall must include, but is not limited to:
8 | 2681 | (c)(2) | A detailed description of the complete construction and monitoring methods to be used. The proposed alternative program, method, device, or process shall be clearly identified. | 2 | 2620 | (c)(2) | A detailed description of the complete construction and monitoring release detection methods and equipment to be used. The proposed alternative program, method, device equipment, or process shall must be clearly identified.
8 | 2681 | (c)(4) | Clear and convincing evidence that the proposed alternative will adequately protect the soil and the beneficial uses of waters of the state from an unauthorized release. | 2 | 2620 | (c)(4) | Clear and convincing evidence Documentation that the proposed alternative will adequately protect the soil and the beneficial uses of waters of the sState from an unauthorized release.
|  |  |  | 2 | 2620 | (g) | The Regional Board must grant a site-specific variance if it determines all the following:
|  |  |  | 2 | 2620 | (g)(2) | There is clear and convincing evidence that the proposed alternative will adequately protect the soil and the beneficial uses of waters of the State from an unauthorized release.
8 | 2681 | (h) | The Regional Water Quality Board shall modify or revoke a variance upon a finding that the proposed alternative does not adequately protect the soil and the beneficial uses of the waters of the state from an unauthorized release. The Regional Water Quality Board shall not modify nor revoke the variance until it has followed procedures comparable to those prescribed in this section and Chapters 1.5 and 6 of Division 3 of Title 23 of the California Code of Regulations. The Regional Water Quality Board shall notify the local agency and the State Water Board of the modification or revocation. The local agency shall modify or revoke the permit for the site. | 2 | 2620 | (j) | The Regional Water Quality Board shall must do all the following:
8 | 2681 | (h) |  | 2 | 2620 | (j)(1) | mModify or revoke a site-specific variance upon a finding that the proposed alternative does not no longer adequately protects the soil and the beneficial uses of the waters of the sState from an unauthorized release.
9 | 2691 | (0) | Procedures for Requesting Additional Standards | 2 | 2621 |  | Procedures for Requesting Additional Construction Standards
9 | 2691 | (a) | A local agency application for additional design and construction standards shall include: | 2 | 2621 | (a) | A local Unified Program Agency application for additional design and construction standards shall must include:
9 | 2691 | (a)(2) | Clear and convincing evidence that the additional standards are necessary to protect the soil and beneficial uses of the waters of the state from unauthorized releases. | 2 | 2621 | (a)(2) | Clear and convincing evidence that the additional standards are necessary to protect the soil and beneficial uses of the waters of the sState from unauthorized releases; and.
9 | 2691 | (a)(3) | Any documents required by the California Environmental Quality Act (Division 13, commencing with section 21000 of the Public Resources Code). | 2 | 2621 | (a)(3) | Any documents environmental information or documentation required by for compliance with the California Environmental Quality Act (Ddivision 13, commencing with section 21000 of the Public Resources Code).
9 | 2691 | (a)(4) | An initial fee of $5,500 | 2 |  |  | An initial fee of $5,500.
9 | 2691 | (b) | The applicant shall be required to pay a fee based on the actual costs of considering the application. The State Water Board will bill the applicant for additional costs or refund any unused portion of the initial fee. | 2 | 2621 | (a)(4) | The applicant shall be required to pay a fee based on the actual costs of considering the application. The State Water Board will bill the applicant for additional costs or refund any unused portion of the initial fee.
9 | 2691 | (d) | The State Water Board may modify or revoke a previously issued authorization allowing the implementation of additional standards if it finds that, based on new evidence, the additional standards are not necessary to adequately protect the soil and beneficial uses of the waters of the state from unauthorized releases. The State Water Board shall neither modify nor revoke the authorization until it has followed procedures comparable to those in Chapters 1.5 and 6 of Division 3 of Title 23 of the California Code of Regulation. | 2 | 2621 | (c) | The State Water Board may must modify or revoke a previously issued authorization allowing the implementation of additional standards if it finds that, based on new evidence, the additional standards are not necessary to adequately protect the soil and beneficial uses of the waters of the sState from unauthorized releases. The State Water Board shall will neither modify nor revoke the authorization until it has followed procedures comparable to those in Cchapters 1.5 and 6 of Ddivision 3 of Ttitle 23 of the California Code of Regulations.
10 | 2715 | (0) | Certification, Licensing, and Training Requirements for Underground Storage Tank Owners, Operators, Facility Employees, Installers, Service Technicians, and Inspectors | 3 | 0 |  | Certification, Licensing, and Training Requirements for Underground Storage Tank Owners, Operators, Facility Employees, Installers, Service Technicians, and Inspectors
|  |  |  | 3 | 2630 |  | Underground Storage Tank Owner and Operator Certification Requirements
10 | 2715 | (a)(1)(B) | A “Designated Underground Storage Tank Operator Identification Form,” located in Appendix XI, identifying the designated UST operator(s) for the facility. | 3 | 2630 | (b) | Within 30 days of installing an underground storage tank system or any change to the designated underground storage tank operator(s), the owner or operator must submit to the Unified Program Agency A "Designated Underground Storage Tank Operator Identification Form,” located in appendix XI , information identifying the designated underground storage tank operator(s) for the facility. The name of each designated underground storage tank operator in the California Environmental Reporting System must be identical to that individual’s name as listed on the individual’s International Code Council UST System Operator certificate.
10 | 2715 | (a)(3) | The owner or operator shall submit a “Designated Underground Storage Tank Operator Identification Form” upon any change of designated UST operator(s) to the local agency no later than 30 days after the change. | 3 | 2630 | (b)
|  |  |  | 3 | 2631 |  | Designated Underground Storage Tank Operator Certification, Facility Training, and Inspection Requirements
10 | 2715 | (b) | Designated UST operators shall possess a current certificate issued by the International Code Council (ICC) indicating that the individual has passed the California UST System Operator exam. The individual shall renew the ICC certification, by passing the California UST System Operator exam, every 24 months. | 3 | 2631 | (a) | Designated underground storage tank operators must possess a current certificate issued by the International Code Council ICC demonstrating that the individual has passed the California UST System Operator exam. The individual shall must renew the ICC International Code Council certification by passing the California UST System Operator exam, every 24 months.
10 | 2715 | (c)(1) | The training for facility employees must be conducted according to the following: | 3 | 2631 | (c)
10 | 2715 | (c)(1)(A) | The initial training of a facility employee shall be conducted through a site‐specific practical demonstration that provides both sharing information and evaluating knowledge for responding to emergencies, leak detection monitoring alarms, spills, and overfills associated with operating the UST system and must include, but is not limited to, the following: | 3 | 2631 | (c) | The initial training of a All facility employee training shall must be conducted through a site‐specific practical demonstration that provides both sharing information and evaluating knowledge for responding to emergencies, leak release detection monitoring system alarms, spills, and overfills associated with operating the UST underground storage tank system. and The facility employee training must include, but is not limited to, at a minimum, all the following information and an evaluation of the retention of that information:
10 | 2715 | (c)(1)(B) | After the initial training of a facility employee, site-specific training must include, but is not limited to, the following: | 3 | 2631 | (c)
10 | 2715 | (c)(1)(A)(i) | The operation of the underground storage tank system in a manner consistent with the facility’s best management practices. | 3 | 2631 | (c)(1) | The operation of the underground storage tank system in a manner consistent with the facility’s best management practices;
10 | 2715 | (c)(1)(A)(ii) | The facility employee’s role with regard to the monitoring equipment as specified in the facility’s monitoring plan. | 3 | 2631 | (c)(2) | The facility employee’s role with regard to regarding the monitoring equipment release detection system(s) as specified in the facility’s UST mMonitoring pPlan(s);
10 | 2715 | (c)(1)(B)(ii) | The facility employee’s role with regard to the monitoring equipment as specified in the facility’s monitoring plan. | 3 | 2631 | (c)(2)
10 | 2715 | (c)(1)(A)(iv) | The name of the contact person(s) for emergencies and monitoring equipment alarms. | 3 | 2631 | (c)(4) | The name of the contact person(s) for emergencies and monitoring equipment release detection system alarms.
10 | 2715 | (c)(1)(B)(iv) | The name of the contact person(s) for emergencies and monitoring equipment alarms. | 3 | 2631 | (c)(4)
10 | 2715 | (c)(4) | Notwithstanding paragraph (3) above, on and after October 1, 2018, upon completion of the facility employee training, the designated UST operator(s) shall provide a signed “Facility Employee Training Certificate,” located in Appendix XII, to the owner or operator for facility employees that have received training. The certificates shall be maintained on-site or off-site at a readily accessible location, if approved by the local agency, and provided to the local agency upon request. The “Facility Employee Training Certificate” satisfies the requirements in paragraph (3), above. | 3 | 2631 | (e) | Notwithstanding paragraph (3) above, on and after October 1, 2018, uUpon completion of the facility employee training, the designated UST underground storage tank operator(s) shall must provide to the owner or operator a signed “Facility Employee Training Certificate,” located in appendix XII, to the owner or operator for 3, identifying the underground storage tank facility, the facility employees that have received training trained, and the date of training. The certificates shall must be maintained on- site or off- site at a readily accessible location, as approved by the local Unified Program Agency, and provided to the local agency Unified Program Agency, the Board, or an independent compliance inspector upon request. The “Facility Employee Training Certificate” satisfies the requirements in paragraph (3), above.
10 | 2715 | (c)(3) | A list of facility employees who have been trained by the designated UST operator(s), shall be maintained on-site or off-site at a readily available location, if approved by the local agency. The list shall be provided to the local agency upon request. The list shall include the dates of training for all facility employees, and the hiring dates for all facility employees hired on or after July 1, 2005. | 3 | 2631 | (e) | A list of facility employees who have been trained by the designated UST operator(s), shall be maintained on-site or off-site at a readily available location, if approved by the local agency. The list shall be provided to the local agency upon request. The list shall include the dates of training for all facility employees, and the hiring dates for all facility employees hired on or after July 1, 2005.
10 | 2716 | (b) | The designated UST operator visual inspection shall identify compliance issues which cause the underground storage tank system to be out of compliance with this chapter and include, but not be limited to, all of the following: | 3 | 2631 | (g) | The designated UST underground storage tank operator visual inspection shall must identify compliance issues which cause the underground storage tank system to be out of compliance with chapter 6.7 of division 20 of the Health and Safety Code or this chapter and must include, but not be limited to at a minimum, all of the following:
10 | 2716 | (b)(2) | Review of the release detection alarm history since the previous visual inspection required by subdivision (a) above, to verify that each alarm condition was documented and responded to appropriately; | 3 | 2631 | (g)(2) | Review of the release detection alarm history since the previous visual inspection required by subdivision (a) above, to verify that each alarm condition was documented and responded to appropriately;
10 | 2716 | (b)(5) | Inspect the spill container for damage and for the presence of any hazardous substance, water, or debris; | 3 | 2631 | (g)(5) | Inspect the spill container containment to check for damage and for the presence of any hazardous substance, water, or debris;
10 | 2716 | (b)(6) | Inspect the fill pipe for obstructions; | 3 | 2631 | (g)(6) | Inspect the fill pipes to check for obstructions and Inspect verify the fill caps are to verify it is securely on the fill pipe in place;
10 | 2716 | (b)(7) | Inspect the fill cap to verify it is securely on the fill pipe; | 3 | 2631 | (g)(6)
10 | 2716 | (c) | The results of the designated UST operator(s) visual inspection shall be recorded on the “Designated Underground Storage Tank Operator Visual Inspection Report” located in Appendix XIII. The report shall include, but not be limited to, all of the following: | 3 | 2631 | (h) | The results of the designated UST underground storage tank operator visual inspection shall must be recorded on the “Designated Underground Storage Tank UST Operator Visual Inspection Report Form” located in appendix XIII 4. The report shall must include, but not be limited to at a minimum, all of the following:
10 | 2716 | (c)(3) | A copy of the alarm history since the previous visual inspection required by subdivision (a) above; | 3 | 2631 | (h)(3) | A copy of the dated release detection alarm history generated by the release detection system since the previous visual inspection required by subdivision (a) above, or if the release detection system cannot generate such a report, a copy of the facility’s alarm log.
10 | 2716 | (0) | Designated UST Operator Visual Inspection | 3 | 2631 |  | Designated UST Operator Visual Inspection
|  |  |  | 3 | 2632 |  | Licensing, Certification, and Training Requirements for Installation
10 |  |  |  | 3 | 2632 | (b) | Any individual performing an underground storage tank system installation or repair work must provide all applicable licenses and certificates of training required pursuant to subdivision (a) for the work being performed upon request by the Unified Program Agency, the Board, or an independent compliance inspector.
|  |  |  | 3 | 2633 |  | Service Technician Licensing, Certification, and Training Requirements
10 | 2715 | (f) | Any individual performing the work of a service technician must meet all of the following requirements: | 3 | 2633 | (a) | Any individual performing the work of a service technician installations or repairs of underground storage tank system components that do not require excavation or backfill, must meet all of the following requirements:
10 | 2715 | (f)(4) | Service technicians shall possess or work under the direct and personal supervision of an individual physically present at the work site who possesses a current certificate from the International Code Council (ICC), indicating the individual has passed the California UST Service Technician exam. The individual shall renew the ICC certification, by passing the California UST Service Technician exam, every 24 months. | 3 | 2633 | (a)(2) | Service technicians shall pPossess or work under the direct and personal supervision of an individual a service technician physically present at the work site who possesses with a current California UST Service Technician certificate from issued by the International Code Council (ICC), indicating demonstrating the individual has passed the California UST Service Technician exam. The individual shall must renew the ICC certification, certificate by passing the California UST Service Technician exam, every 24 months.; and
10 | 2715 | (f)(2) | Be trained and certified by the manufacturer of the equipment as follows: | 3 | 2633 | (a)(3) | Be trained and certified by Possess training and certification from the manufacturer of the underground storage tank component or test equipment as follows:
10 | 2715 | (f)(2)(C) | On and after October 1, 2018, for service technicians conducting spill container testing pursuant to section 2637.1, this training and certification may be obtained through the manufacturer of the spill container being tested or through the developer of the testing equipment or test method being used in accordance with section 2637.1(b). | 3 | 2633 | (a)(3)(B) | On and after October 1, 2018, for service technicians Before performing work on spill containment, including conducting spill container testing pursuant to section 2637.1 2664, this obtain training and certification may be obtained through from the manufacturer of the spill container containment being tested or through the developer of the testing equipment or test method being used in accordance with section 2637.1(b) 2664(b).
10 | 2715 | (f)(2)(A) | For service technicians conducting secondary containment testing pursuant to section 2637, this training and certification may be obtained through the manufacturer of the secondary containment system being tested or through the developer of the testing equipment or test method being used in accordance with section 2637(c). | 3 | 2633 | (a)(3)(D) | For service technicians Before conducting secondary containment testing pursuant to section 2637 2666, this obtain training and certification may be obtained through the manufacturer of the secondary containment system being tested or through the developer of the testing equipment or test method being used in accordance with section 2637(c) 2666(c).
10 | 2715 | (f)(2) |  | 3 | 2633 | (c) | Any individual performing the work of a service technician must provide all applicable licenses and certificates of training required pursuant to subdivision (a) for the work being performed upon request by the Unified Program Agency, the Board, or an independent compliance inspector.
|  |  |  | 3 | 2634 |  | Inspector Certification and Training Requirements
10 | 2715 | (g)(1) | Possess a current inspector certificate issued by the International Code Council (ICC), indicating the individual has passed the ICC California UST Inspector exam. Local agency inspectors are subject to this requirement 180 days from the date of hire. | 3 | 2634 | (a)(1) | Within 180 days from the date that an individual begins to perform any of the duties of a Unified Program Agency inspector, the individual must Ppossess a current inspector certificate issued by the International Code Council (ICC), indicating demonstrating the individual has passed the ICC International Code Council California UST Inspector exam. Local agency inspectors are subject to this requirement 180 days from the date of hire.
10 | 2715 |  |  | 3 | 2634 | (a)(3) | Only Unified Program Agency inspectors and independent compliance inspectors working on behalf of a Unified Program Agency with a current inspector certificate issued by International Code Council may approve submittals to the California Environmental Reporting System.
3 | 0 | (0) | New Underground Storage Tank Design, Construction, And Monitoring Requirements | 4 | 0 |  | New Underground Storage Tank Design, Construction, Aand Operation Monitoring Requirements for Underground Storage Tank Systems
3 | 2631 | (0) | Design and Construction Requirements for New Underground Storage Tanks | 4 | 2640 |  | Design and Construction Requirements Standards for New All Underground Storage Tank Systems
3 | 2631.1 | (0) | Compatibility and Permeability Testing Requirements for all New Underground Storage Tanks | 4 | 2640 | (a) | Compatibility and Permeability Testing Requirements for all New Underground Storage Tanks
3 | 2631.1 | (a) | Owners and operators must use an underground storage tank system made of or lined with materials that are compatible with the substance stored in the underground storage tank system. | 4 | 2640 | (a) | Compatibility – Owners and operators must use an uUnderground storage tank systems must be constructed made of or lined with materials that are compatible with the stored hazardous substance stored in the underground storage tank system. Materials used in construction or repairs and upgrades shall must be compatible with the materials used to construct the underground storage tank system existing materials and shall must not be subject to deterioration due to contact with the hazardous substances being stored.
6 | 2660 | (m) | Materials used in repairs and upgrades shall be compatible with the underground storage tank system existing materials and shall not be subject to deterioration due to contact with the hazardous substances being stored. | 4 | 2640 | (a)
3 | 2631.1 | (b) | For underground storage tank system components installed on or after July 1, 2004, the applicable approvals required in subsections 2631(b) and (d) shall include a list of the compatible products tested and the measured product permeation rates, if such testing is required by the industry code or engineering standard used to evaluate the component. These results shall be provided to the local agency upon request. | 4 | 2640 | (a) | For underground storage tank system components installed on or after July 1, 2004, the applicable approvals required in subsections 2631(b) and (d) shall include a list of the compatible products tested and the measured product permeation rates, if such testing is required by the industry code or engineering standard used to evaluate the component. These results shall be provided to the local agency upon request.
|  |  |  | 4 | 2640 | (a)(1) | Owners or operators must demonstrate compatibility using the following documentation:
|  |  |  | 4 | 2640 | (a)(1)(C) | Spill containment, overfill prevention equipment, and ancillary equipment:
|  |  |  | 4 | 2640 | (a)(1)(C)(i) | An independent testing organization approval for compatibility with the hazardous substances stored;
|  |  |  | 4 | 2640 | (a)(1)(D) | Release detection equipment:
|  |  |  | 4 | 2640 | (a)(1)(D)(i) | An independent third party approval for compatibility with the hazardous substances stored; or
10 | 2712 | (b)(5) | On and after October 1, 2018, documentation of the underground tank system’s compatibility with the stored substance, in accordance with section 2711(c), shall be maintained for as long as the system is used to store the specific substance; and | 4 | 2640 | (a)(2) | On and after October 1, 2018, dDocumentation of the underground storage tank system’s compatibility with the stored substance, in accordance with section 2711(c), shall hazardous substance stored must be maintained for as long as the system is used to store the specific hazardous substance.; and
3 | 2631 | (a) | All new underground storage tanks including associated piping used for the storage of hazardous substances shall have primary and secondary containment. Primary containment shall be product-tight. Secondary containment may be manufactured as an integral part of the primary containment or it may be constructed as a separate containment system. Secondary containment systems shall be designed and constructed such that the secondary containment system can be periodically tested in accordance with section 2637. | 4 | 2640 | (b) | All new uContainment – Underground storage tanks including associated piping used for the storage of hazardous substances shall must have primary and secondary containment. Primary containment shall be product-tight. Secondary containment may be manufactured as an integral part of the primary containment or it may be constructed as a separate containment system. Secondary containment systems shall be designed and constructed such that the secondary containment system can be periodically tested in accordance with section 2637 that meet the requirements of this section.
3 | 2631 | (a) |  | 4 | 2640 | (b)(01) | Primary containment shall must be product tight. Secondary containment may be manufactured as an integral part of the primary containment or it may be constructed as a separate containment system. Secondary containment systems shall must be designed and constructed such that the secondary containment system can be monitored in accordance with sections 2651 and 2652, and periodically tested in accordance with section 2637 2666.
3 | 2631 | (b) | Except as provided in subdivision (j) below, the design and construction of all primary containment including any integral secondary containment system, shall be approved by an independent testing organization in accordance with industry codes, voluntary consensus standards, or engineering standards. Except as provided in subdivision (j) below, all other components used to construct the primary containment system, such as special accessories, fittings, coatings or linings, monitoring systems, and level controls shall also be approved by an independent testing organization. These requirements became effective on July 1, 1991 for underground storage tanks; January 1, 1992 for piping; and January 1, 1995 for all other components. The exterior surface of underground storage tanks shall bear a marking, code stamp, or label showing the following minimum information: | 4 | 2640 | (b)(02) | Except as provided in subdivision (j) below, tThe design and construction of all primary containment, including any integral secondary containment system, shall and all other components used to construct the primary containment that may come into contact with the hazardous substance stored, such as special accessories, fittings, coatings or linings, must be approved by an independent testing organization in accordance with industry codes, voluntary consensus standards, or engineering standards. Except as provided in subdivision (j) below, all other components used to construct the primary containment system, such as special accessories, fittings, coatings or linings, monitoring systems, and level controls shall also be approved by an independent testing organization. These requirements became effective on July 1, 1991 for underground storage tanks; January 1, 1992 for piping; and January 1, 1995 for all other components. The exterior surface of underground storage tanks shall bear a marking, code stamp, or label showing the following minimum information:.
3 | 2631 | (d) | A secondary containment system which is not an integral part of primary containment shall be designed and constructed according to an engineering specification approved by a state registered professional engineer or according to a nationally recognized industry code or engineering standard. The engineering specification shall include the construction procedures. Materials used to construct the secondary containment system shall have sufficient thickness, density, and corrosion resistance to prevent structural weakening or damage to the secondary containment system as a result of contact with any released hazardous substance. The following requirements apply to these secondary containment systems: | 4 | 2640 | (b)(03) | A sSecondary containment system which is not an integral part of primary containment shall must be designed and constructed, operated, and maintained in accordance with according to an engineering specification approved by an independent testing organization or approval by a state California registered professional engineer or according to a nationally recognized industry code or engineering standard. The engineering specification shall must include the construction, testing, and maintenance procedures. Materials used to construct the secondary containment system shall must have sufficient thickness, density, and corrosion resistance to prevent structural weakening or damage to the secondary containment system as a result of contact with any released hazardous substance. The following requirements apply to these non-integral secondary containment systems:
3 | 2631 | (d)(1) | The secondary containment system shall be constructed to contain at least the following volumes: | 4 | 2640 | (b)(03)(A) | The secondary containment system shall must be constructed to contain at least the following volumes:
3 | 2631 | (d)(1)(A) | One hundred percent of the usable capacity of the primary containment system where only one primary container is within the secondary containment system. | 4 | 2640 | (b)(03)(A)(i) | One hundred percent of the usable capacity of the primary containment system where only one primary container is within the secondary containment system.
3 | 2631 | (d)(1)(B) | In the case of multiple primary containers within a single secondary containment system, the secondary containment system shall be large enough to contain 150 percent of the volume of the largest primary container within it, or 10 percent of the aggregate internal volume of all primary containers within the secondary containment system, whichever is greater. When all primary containers are completely enclosed within the secondary containment system, the restrictions of this subdivision do not apply. | 4 | 2640 | (b)(03)(A)(ii) | In the case of multiple primary containers within a single secondary containment system, the secondary containment system shall must be large enough to contain 150 percent of the volume of the largest primary container within it, or 10 percent of the aggregate internal volume of all primary containers within the secondary containment system, whichever is greater. When all primary containers are completely enclosed within the secondary containment system, the restrictions of this subdivision subparagraph do not apply.
3 | 2631 | (d)(2) | If the secondary containment system is open to rainfall, it shall be constructed to accommodate the volume of precipitation which could enter the secondary containment system during a 24-hour, 25-year storm in addition to the volume specified in subdivision (d)(1) above. | 4 | 2640 | (b)(03)(B) | If the secondary containment system is open to rainfall, it shall must be constructed, operated, and maintained to accommodate the volume of precipitation which could enter the secondary containment system during a 24-hour, 25-year storm in addition to the volume specified in subdivision (d)(1) above subparagraph (A).
3 | 2631 | (d)(3) | If backfill material is placed in the secondary containment system, the volumetric requirements for the pore space shall be equal to the requirement in subdivision (d)(1) above. The available pore space in the secondary containment system backfill shall be determined using standard engineering methods and safety factors. The specific retention and specific yield of the backfill material, the location of any primary container within the secondary containment, and the proposed method of operation for the secondary containment system shall be considered in determining the available pore space. | 4 | 2640 | (b)(03)(C) | If backfill material is placed in the secondary containment system, the volumetric requirements for the pore space shall must be equal to the requirement in subdivision (d)(1) above subparagraph (A). The available pore space in the secondary containment system backfill shall must be determined using standard engineering methods and safety factors. The specific retention and specific yield of the backfill material, the location of any primary container within the secondary containment, and the proposed method of operation for the secondary containment system shall must be considered in determining the available pore space.
3 | 2631 | (d)(4) | The secondary containment system shall be equipped with a collection system to accumulate, temporarily store, and permit removal of any liquid within the system. | 4 | 2640 | (b)(03)(D) | The secondary containment system shall must be equipped with a collection system to accumulate, temporarily store, and permit allow removal of any liquid within the system.
3 | 2631 | (g) | Underground storage tanks with secondary containment systems shall be so designed and installed so that any loss of a hazardous substance from the primary containment will be detected by an interstitial monitoring device or method. | 4 | 2640 | (b)(04) | Underground storage tanks with sSecondary containment systems shall must be constructed, operated, and maintained so designed and installed so that any loss of a liquid hazardous substance from the primary containment liquid will be detected by an interstitial monitoring device or visual monitoring method and readily demonstrate continuity within a zone.
3 | 2631 | (f) | Underground storage tanks with integral secondary containment systems, which satisfy the construction requirements of subdivision (b) above, fulfill the volumetric requirements for secondary containment specified in subdivision (d)(1) above. | 4 | 2640 | (b)(05) | Underground storage tanks with integral secondary containment systems, which satisfy satisfies the construction requirements of subdivision (b)(2) above, fulfill the volumetric requirements for secondary containment specified in subdivision (d)(1) above subparagraph (b)(3)(A).
3 | 2635 | (e)(5) | Two or more primary containment systems shall not use the same secondary containment system if the primary containment systems store materials that in combination may cause a fire or explosion, or the production of a flammable, toxic, or poisonous gas, or the deterioration of any part of the primary or secondary containment system. | 4 | 2640 | (b)(07) | Two or more primary containment systems shall must not use the same secondary containment system if the primary containment systems store materials that in combination may cause a fire or explosion, or the production of a flammable, toxic, or poisonous gas, or the deterioration of any part of the primary or secondary containment system.
3 | 2631 | (h) | An underground storage tank which contains motor vehicle fuel and which is designed with an integral secondary containment system shall provide 100 percent secondary containment unless it is equipped with overfill prevention equipment in accordance with section 2635(c)(1)(C). In this case, the top portion of the tank, no greater than two feet wide along the length of the tank, may be single-walled. | 4 | 2640 | (b)(08) | An underground storage tank which contains motor vehicle fuel and which is designed constructed with an integral secondary containment system shall must provide 100 percent secondary containment unless it is equipped with overfill prevention equipment in accordance with section 2635(c)(1)(C). In this case, the top portion of the tank, no greater than two feet wide along the length of the tank, may be single-walled. The tank may be single-walled up to 12 inches away from the top center line of the tank if it is equipped with overfill prevention equipment such that the hazardous substance cannot contact any portion of the single-walled construction.
3 | 2636 | (c)(1) | Primary piping in contact with hazardous substances under normal operating conditions shall be installed inside a secondary containment system which may be a secondary pipe, vault, or a lined trench. All secondary containment systems shall be sloped so that all releases will flow to a collection sump located at the low point of the underground piping. | 4 | 2640 | (b)(09) | Primary piping in contact with hazardous substances under normal operating conditions shall be installed inside a secondary containment system which may be a secondary pipe, vault, or a lined trench. All piping secondary containment systems shall must be sloped so that all releases will flow to a collection containment sump located at the low point of the underground piping secondary containment.
10 | 2712 | (j) | All primary containment shall be product-tight. | 4 | 2640 | (b)(01)
3 | 2636 | (a) | Except as provided below, piping connected to tanks which were installed after July 1, 1987, shall have secondary containment that complies with the requirements of section 2631 for new underground storage tanks. This requirement does not apply to any of the following: | 4 | 2640 | (b)(10) | Except as provided below, All connected piping connected to tanks which were installed after July 1, 1987, shall have secondary containment that complies with the requirements of section 2631 for new underground storage tanks. This requirement does not apply to any of the following must be secondarily contained except unburied fuel delivery piping at marinas exempt pursuant to section 2612(n), unburied fuel piping connected to an emergency tank system exempt pursuant to section 2612(o) and the following:
3 | 2636 | (a)(1) | Vent or tank riser piping, provided the primary containment system is equipped with overfill prevention equipment meeting the requirements specified in sections 2635(c)(1)(B) or (C); | 4 | 2640 | (b)(10)(A) | Vent or and tank riser piping attached to Type 1 underground storage tanks, provided the primary containment system tank is equipped with overfill prevention equipment meeting the requirements specified in sections 2635(c)(1)(B) or (C) subparagraph (B) or (C) of subdivision (f)(1);
3 | 2636 | (a)(2) | Vapor recovery piping if designed so that it cannot contain liquid-phase product; or | 4 | 2640 | (b)(10)(B) | Vapor recovery piping attached to Type 1 underground storage tanks if constructed to designed so that it can not contain liquid-phase product hazardous substance; or and
3 | 2636 | (a)(3) | Suction piping if the piping is designed, constructed, and installed as follows: | 4 | 2640 | (b)(10)(C) | Suction piping if the piping is designed, constructed, and installed as follows attached to Type 1 underground storage tanks that meets all the following:
3 | 2636 | (a)(3)(B) | The below-grade piping is sloped so that the contents of the pipe will drain back into the storage tank if the suction is released (gravity-flow piping); | 4 | 2640 | (b)(10)(C)(ii) | The below-grade piping is sloped so that the contents of the pipe will drain back into the storage tank if the suction is released (gravity-flow piping);
3 | 2635 | (b) | All underground storage tanks shall be equipped with a spill container that collects any hazardous substances spilled during product delivery operations to prevent the hazardous substance from entering the subsurface environment. The spill container shall meet all of the following: | 4 | 2640 | (e) | All underground storage tanks shall Spill Containment - Each tank fill point must be equipped with a spill container that containment to collects any hazardous substances spilled during product delivery operations to and prevent the hazardous substance from escaping to entering the subsurface environment when the tank is filled. The spill container shall meet all of the following containment must:
3 | 2635 | (b)(3) | It shall have a drain valve which allows drainage of the collected spill into the primary container or provide a means to keep the spill container empty. | 4 | 2640 | (e)(3) | It shall have a drain valve which allows drainage of the collected spill into the primary container or provide Have a means to keep the spill container containment empty.
3 | 2635 | (c)(2) | The local agency may waive the requirement for overfill prevention equipment where the tank inlet exists in an observable area, the spill container is adequate to collect any overfill, and the tank system is filled by transfers of no more than 25 gallons at one time. | 4 | 2640 | (f)(2) | The local Unified Program Agency may waive or modify the requirement for overfill prevention equipment where the tank inlet exists is located in an observable area, the spill container is adequate to collect any overfill, and the tank is filled by transfers of no more than 25 gallons at one time, and the owner or operator is not utilizing the single-walled vent or tank riser piping exemption for Type 1 underground storage tanks in subdivision (b)(10)(A). The Unified Program Agency may revoke an exemption if the system fails to prevent overfills.
|  |  |  | 4 | 2640 | (g) | Manways – All tank entries must be through a manway. If a manway must be installed, the manway must be installed in accordance with the tank manufacturer’s written guidelines, an industry code, or an engineering standard.
3 | 2636 | (g)(2) | Under-dispenser containment shall be designed, constructed, installed, and monitored in accordance with section 2631 and subdivisions (c)(2), (e), and (f) above. | 4 | 2640 | (h) | Under-dispenser containment – All dispensers must be fitted with Uunder-dispenser containment shall be that is designed, constructed, installed, and monitored pursuant to in accordance with sections 2631 and subdivisions (c)(2), (e), and (f) above 2642(a), 2642(f), and 2652(a).
3 | 2636 | (g) | Under-dispenser containment shall be designed, constructed, and installed in accordance with the following: | 4 | 2640 | (h)
3 | 2636 | (g)(1) | Owners or operators of an underground storage tank system shall have the system fitted with under-dispenser containment, or an approved under-dispenser spill containment or control system. | 4 | 2640 | (h)
|  |  |  | 4 | 2641 |  | Additional Design and Construction Standards for Type 2 and Type 3 Underground Storage Tanks
|  |  |  | 4 | 2641 | (a) | Underground storage tanks installed on or after July 1, 2026 must bear a marking, code stamp, or label, located within the perimeter of the sump collar, including the following:
|  |  |  | 4 | 2641 | (a)(6) | Openings not equipped with a striker plate (if any).
|  |  |  | 4 | 2641 | (b) | Secondary containment systems for Type 2 and Type 3 underground storage tanks must be constructed, operated, and maintained to prevent water intrusion. Backfill material must not be added to secondary containment.
6 | 2661 | (0) | Requirements for Repairing Underground Storage Tank | 4 | 2642 |  | Installation and Repair Requirements for Repairing Underground Storage Tank
6 | 0 | (0) | Underground Storage Tank Repair and Upgrade Requirements | 4 | 2642 |  | Underground Storage Tank Repair and Upgrade Requirements
10 | 2715 | (e) |  | 4 | 2642 | (c) | Underground storage tank systems must be installed by persons meeting the requirements of sections 2632 and 2633, as applicable.
3 | 2636 | (c)(2) | Primary piping and secondary containment systems shall be installed in accordance with an industry code of practice developed in accordance with voluntary consensus standards. The owner or operator shall certify that the piping was installed in accordance with the above requirements of section 2635(f). The certification shall be made on the “UST Certification of Installation/ Modification” submittal element in the California Environmental Reporting System or a local reporting portal. | 4 | 2642 | (d) | Primary piping and secondary containment systems shall All piping must be installed in accordance with manufacturer’s installation procedures, or an industry code of practice developed in accordance with voluntary consensus standards if requirements are not specified by the manufacturer. Notwithstanding paragraphs (1) and (3) of section 2640(b), steel piping installed on or after January 1, 2026, must be constructed of a minimum factory coated black steel meeting ASTM A53, with minimum schedule 40 thickness if used for primary containment and minimum schedule 10 thickness if used for secondary containment. The owner or operator shall certify that the piping was installed in accordance with the above requirements of section 2635(f). The certification shall be made on the “UST Certification of Installation/ Modification” submittal element in the California Environmental Reporting System or a local reporting portal.
3 | 2635 | (a)(6) | All underground storage tanks shall be installed according to a code of practice developed in accordance with voluntary consensus standards and the manufacturer’s written installation instructions. The owner or operator shall certify that the underground storage tank was installed in accordance with the above requirements as required by subdivision (f) of this section. | 4 | 2642 | (e) | All uUnderground storage tanks systems shall must be installed, operated, and maintained according to a code of practice developed in accordance with voluntary consensus standards and the manufacturer's written installation instructions. specifications, industry codes, and engineering standards. The owner or operator shall certify that the underground storage tank was installed in accordance with the above requirements as required by subdivision (f) of this section.
3 | 2635 | (a)(7) | All underground storage tanks subject to flotation shall be anchored using methods specified by the manufacturer or, if none exist, shall be anchored according to the best engineering judgment. | 4 | 2642 | (e)(1) | All underground storage tTanks subject to flotation shall installed on or after January 1, 2027, must be anchored to prevent flotation using methods specified by the manufacturer or, if none exist, shall be anchored according to the best engineering judgment, an industry code or engineering standard, or in accordance with an engineering specification approved by a state registered professional engineer.
3 | 2635 | (f) | Owners or their agents shall certify that the installation of the tanks and piping meets the conditions in paragraph (1) through (4) below. The certification shall be made on the “UST Certification of Installation/ Modification” submittal element in the California Environmental Reporting System or a local reporting portal. | 4 | 2642 | (g) | Within 30 days of an inspection by the Unified Program Agency or special inspector of an installation, the Oowners or their agents shall operator must certify the installation of tanks and piping by submitting to the Unified Program Agency in the “UST Certification of Installation/Modification” data elements a certification that the installation of the underground storage tanks and piping, including containment sumps, meets all the following conditions: conditions in paragraph (1) through (4) below. The certification shall be made on the “UST Certification of Installation/ Modification” submittal element in the California Environmental Reporting System or a local reporting portal.
3 | 2635 | (f)(1) | The installer has met the requirements set forth in sections 2715(d) and (e); | 4 | 2642 | (g)(1) | The installer has met the requirements set forth in sections 2715(d) and (e) 2632;
6 | 2660 | (k) | Local agencies shall not approve a repair or upgrade unless it can be demonstrated that the underground storage tank system is structurally sound and the method of repair or upgrade will prevent unauthorized releases due to structural failure or corrosion during the operating life of the underground storage tank system. | 4 | 2642 | (l) | Local agencies shall not The Unified Program Agency only may approve a repair or upgrade unless if it can be demonstrated that the underground storage tank system is structurally sound, and the method of repair or upgrade will prevent unauthorized releases due to structural failure or corrosion during the operating life of while the underground storage tank system is operational. Unified Program Agency approvals of any repair to the primary containment must be in writing.
|  |  |  | 4 | 2643 |  | Operating Requirements for Underground Storage Tanks
|  |  |  | 4 | 2643 | (b) | All underground storage tanks must be operated and maintained to manufacturer’s specifications.
10 | 2712 | (f) | Within 30 days of receiving an inspection report from either the local agency or the special inspector, the permit holder shall implement the corrections specified in the inspection report and comply with the permit conditions. The corrective action shall include all of the recommendations made by the local agency or special inspector. The local agency may waive the implementation of any of the special inspector’s recommendations based on a demonstration by the permit holder to the local agency’s satisfaction that failure to implement the recommendation will not cause an unauthorized release. | 4 | 2649 | (t) | Within 30 days of receiving an inspection report from either the local agency or the special inspector, the permit holder shall implement the corrections specified in the inspection report and comply with the permit conditions. The corrective action shall include all of the recommendations made by the local agency or special inspector. The local agency may waive the implementation of any of the special inspector’s recommendations based on a demonstration by the permit holder to the local agency’s satisfaction that failure to implement the recommendation will not cause an unauthorized release.
|  |  |  | 4 | 2643 | (c) | For each minor violation issued by the Unified Program Agency or the Board, the owner or operator must correct the violation in accordance with section 25404.1.2 of the Health and Safety Code.
|  |  |  | 4 | 2643 | (d) | For all other violations issued or recommendations contained in an inspection report by the Unified Program Agency, the Board, or a special inspector, the owner or operator must correct the violation, implement the recommendation, or demonstrate why the recommendation should not be implemented in accordance with section 25288 of the Health and Safety Code.
4 | 2643 | (f)(2) | An independent third party testing laboratory shall evaluate and approve the method using a voluntary consensus standard that is intended for the method being evaluated; | 5 | 2651 | (d)(2) | An independent third-party testing laboratory shall must evaluate and approve the method using a voluntary consensus standard that is intended for the method being evaluated. The evaluation results must contain the same information and must be reported following the same general format as the EPA standard results sheet for any corresponding EPA method; or
4 | 2643 | (f)(4) | The evaluation results referred to paragraphs (2) and (3) shall contain the same information and shall be reported following the same general format as the EPA standard results sheet as any corresponding EPA test procedure. | 5 | 2651 | (d)(2)
4 | 2643 | (f)(3) | An independent third party testing laboratory shall evaluate and approve the method using a procedure deemed equivalent to an EPA procedure. Any resultant certification shall include a statement by the association or laboratory that the conditions under which the test was conducted were at least as rigorous as those used in the EPA standard test procedure. This certification shall include statements that: | 5 | 2651 | (d)(3) | An independent third-party testing laboratory shall must evaluate and approve the method using a procedure deemed equivalent to an EPA procedure method. Any resultant certification shall must include a statement by the association or laboratory that the conditions under which the test was conducted were at least as rigorous as those used in the EPA standard test procedure method. This certification shall include must contain the same information and must be reported following the same general format as the EPA standard results sheet for any corresponding EPA method, and must contain statements that:
3 | 2632 | (c)(2)(A) | The interstitial space of the tank shall be monitored using a continuous monitoring system which meets the requirements of section 2643(f). | 5 | 2651 | (e) | The interstitial space Except as provided in subdivision (g), secondary containment of Type 1 and Type 2 underground storage the tanks shall must be monitored using a continuous monitoring interstitial release detection system which meets the requirements of section 2643(f) subdivision (d). The continuous monitoring release detection system shall be connected to must activate an audible and visual alarm system when a release is detected and be approved by the local agency Unified Program Agency.
3 | 2632 | (c)(2)(B) | The continuous monitoring system shall be connected to an audible and visual alarm system approved by the local agency. | 5 | 2651 | (e)
|  |  |  | 5 | 2651 | (f) | Interstitial spaces of Type 3 underground storage tanks must be monitored using a continuous vacuum, pressure, or hydrostatic interstitial release detection system which meets the requirements of subdivision (d). The continuous release detection system must activate an audible and visual alarm when a release is detected and be approved by the Unified Program Agency.
3 | 2636 | (0) | Design, Construction, Installation, Testing, and Monitoring Requirements for Piping | 5 | 2652 |  | Design, Construction, Installation, Testing, and Additional Monitoring Requirements for Piping
3 | 2636 | (f) | Underground piping with secondary containment, including under-dispenser piping with secondary containment, shall be equipped and monitored with monitoring systems as follows: | 5 | 2652 | (a) | Underground piping with secondary containment, including under-dispenser piping with secondary containment, shall Piping must be equipped and monitored with monitoring systems as follows:
3 | 2636 | (f)(1) | All secondary containment, including under-dispenser containment, and under-dispenser spill control or containment systems shall be equipped with a continuous monitoring system that either activates an audible and visual alarm or stops the flow of product at the dispenser when it detects a leak. | 5 | 2652 | (a)(1)(A) | All secondary containment Except as provided in section 2651(g), piping secondary containment, including under-dispenser containment, and under-dispenser spill control or containment systems shall must be equipped with a continuous monitoring interstitial release detection system that either activates an audible and visual alarm, or stops the flow of product hazardous substance at the dispenser when it detects a leak a release from the piping is detected.
|  |  |  | 5 | 2652 | (a)(1)(B) | Mechanical release detection equipment used to continuously monitor under-dispenser containment, including an impact shear valve, which fails to function properly at any time, cannot be repaired and must be replaced with continuous electronic release detection equipment to meet the requirements of this subdivision.
|  |  |  | 5 | 2652 | (a)(1)(C) | On or after July 1, 2026, at facilities that are not routinely staffed, underground storage tank systems with pressurized piping that are not emergency tank systems must have a continuous interstitial release detection system that shuts off the flow of hazardous substance through the piping when it detects a release from the piping or the release detection system malfunctions.
3 | 2636 | (f)(2) | Automatic line leak detectors shall be installed on underground pressurized piping and shall be capable of detecting a three gallons per hour leak rate at 10 pounds per square inch within one hour with a probability of detection of at least 95 percent and a probability of false alarm no greater than five percent, and shall restrict or shut off the flow of product through the piping when a leak is detected. | 5 | 2652 | (a)(2) | Automatic Line leak detectors shall must be installed on underground buried pressurized pipe piping and shall must be capable of detecting a three gallons per hour release rate at 10 pounds per square inch within one hour with a probability of detection of at least 95 percent and a probability of false alarm no greater than five percent, and shall must restrict or shut off the flow of product hazardous substance through the piping when it detects a leak is detected release.
3 | 2636 | (f)(5)(A) | Underground pressurized piping connected to an emergency generator tank system installed before October 1, 2018, may use a continuous monitoring system as described in paragraph (1) above, which activate an audible and visual alarm in the event of a leak or a malfunction of the monitoring system satisfy the automatic line leak detector requirement of paragraph (2) above. The monitoring system shall be checked at least daily by either remote electronic access or on-site visual inspections. A log of daily checks shall be available for local agency review upon request. By October 13, 2018, all underground pressurized piping connected to an emergency generator tank system shall meet section 2666(f). | 5 | 2652 | (a)(2)(A) | Underground pressurized pPiping connected to an emergency generator tank system installed before October 1, 2018, may use a continuous monitoring system line leak detector as described in paragraph (12) above, which activates an audible and visual alarm in the event of a leak or a malfunction of lieu of shutting off or restricting flow through the piping when a release from the piping is detected or the line leak detector or monitoring system satisfy the automatic line leak detector requirement of paragraph (2) above malfunctions. The monitoring system shall be checked at least daily by either remote electronic access or on-site visual inspections. A log of daily checks shall be available for local agency review upon request. By October 13, 2018, all underground pressurized piping connected to an emergency generator tank system shall meet section 2666(f).
|  |  |  | 5 | 2652 | (a)(2)(B) | A continuous vacuum, pressure, or hydrostatic interstitial release detection system that shuts off the flow of hazardous substance through the piping when a release from the piping is detected or the release detection system malfunctions satisfies the line leak detector requirement.
|  |  |  | 5 | 2652 | (a)(2)(C) | Piping connected to an emergency tank system may use a vacuum, pressure, or hydrostatic interstitial release detection system as described in subparagraph (B), which activates an audible and visual alarm in lieu of shutting off flow through the piping when a release from the piping is detected or the release detection system malfunctions.
3 | 2636 | (f)(3) | Monitoring shall be conducted on all underground pressurized piping with secondary containment at least once every 12 months at a pressure designated by the equipment manufacturer, provided that the method is capable of detecting a minimum release equivalent to 0.1 gallons per hour defined at 150 percent of the normal operating pressure of the product piping system at the test pressure with at least a 95 percent probability of detection and not more than a five percent probability of false alarm. | 5 | 2652 | (a)(3) | Monitoring shall Tightness testing must be conducted on buried all underground pressurized piping connected to Type 1 and Type 2 underground storage tanks with secondary containment at least once every 12 months using a release detection method or equipment at a pressure designated by the equipment manufacturer, provided that the method is capable of detecting a minimum release equivalent to 0.1 gallons per hour defined at 150 percent of the normal piping system operating pressure of the product piping system, with at the test pressure with at least east a 95 percent probability of detection and not more than a five percent probability of false alarm.
3 | 2636 | (f)(4) | Continuous monitoring systems as described in paragraph (1) above, satisfy the tightness testing requirement of paragraph (3) above, if both of the following conditions are met: | 5 | 2652 | (a)(4) | Continuous monitoring release detection systems as described in paragraph (1) above, satisfy the tightness testing requirement of paragraph (3), above if both of the following conditions are met:
3 | 2636 | (f)(4)(A) | The monitoring system shuts down the pump or stops the flow of product at the dispenser when a leak is detected in the under-dispenser containment. | 5 | 2652 | (a)(4)(A) | The monitoring release detection system shuts down the pressure pump or stops the flow of product hazardous substance at the dispenser when a leak release is detected in the under-dispenser containment.; and
3 | 2636 | (f)(4)(B) | The monitoring system for all product piping other than that contained in the under-dispenser containment is fail safe, and shuts down the pump when a leak is detected. | 5 | 2652 | (a)(4)(B) | The monitoring release detection system for all product piping buried pressurized hazardous substance piping other than that contained in the under-dispenser containment is fail safe and shuts down the pressure pump when a leak release from the piping is detected.
|  |  |  | 5 | 2652 | (b) | Piping connected to Type 3 underground storage tanks must be monitored by a continuous vacuum, pressure, or hydrostatic interstitial release detection system in accordance with subdivisions (d) and (e) of section 25290.1 of the Health and Safety Code.
|  |  |  | 5 | 2652 | (c) | Piping monitored by continuous vacuum, pressure or hydrostatic interstitial monitoring must:
|  |  |  | 5 | 2652 | (c)(1) | Be configured to facilitate testing required pursuant to section 2663(a); and
|  |  |  | 5 | 2652 | (c)(2) | Be configured so that continuity can be confirmed for each zone to the extent practical as approved by the Unified Program Agency during testing required pursuant to sections 2642(f) and 2663(a).
|  |  |  | 6 | 0 |  | Testing Requirements for Underground Storage Tanks
|  |  |  | 6 | 2660 |  | General Requirements for Testing
3 | 2638 | (e) | The owner or operator shall notify the local agency at least 48 hours prior to conducting the installation, repair, replacement, calibration, or certification of monitoring equipment. | 6 | 2660 | (a) | Notification – The underground storage tank owner or operator shall must notify the local agency at least 48 hours prior to conducting the installation, repair, replacement, calibration, or certification of monitoring equipment Unified Program Agency of upcoming testing in accordance with section 2614.
3 | 2637 | (g) | Owners and operators of underground storage tanks must notify the local agency at least 48 hours prior to conducting the secondary containment test. | 6 | 2660 | (a)
3 | 2637.1 | (f) | Owners or operators shall notify the local agency at least 48 hours prior to conducting the spill container test. | 6 | 2660 | (a)
3 | 2637.2 | (f) | Owners or operators shall notify the local agency at least 48 hours prior to conducting the inspection. | 6 | 2660 | (a)
4 | 2644.1 | (a)(4) | Owners and operators of underground storage tanks subject to the requirements of this section must notify the local agency at least 48 hours prior to conducting the enhanced leak detection test. | 6 | 2660 | (a)
4 | 2643 | (g) | The underground storage tank owner or operator shall notify the local agency 48 hours before conducting a tank or piping integrity test. Within 30 days of completion of an underground storage tank or piping integrity test, the tank owner or operator shall submit a report to the local agency through the California Environmental Reporting System or a local reporting portal. The results of any underground storage tank tests, other than those required by this article, performed on the underground storage tank or piping to detect an unauthorized release shall be submitted by the owner or operator to the local agency through the California Environmental Reporting System or a local reporting portal within 30 days of completion of the test. The report shall be presented in written format, as appropriate, and shall be at a level of detail appropriate for the release detection method used. | 6 | 2660 | (a) & (d)
3 | 2638 | (d) | Owners or operators shall submit a completed “Monitoring System Certification Form” to the local agency within 30 days after completion of the inspection. | 6 | 2660 | (d) | Test Results – Underground storage tank Oowners or operators shall must submit a completed “Monitoring System Certification Form” test results to the local agency Unified Program Agency within 30 days after completion of the inspection of performing the test.
3 | 2637 | (f) | On and after October 1, 2018, underground storage tank owners and operators shall submit a copy of the “Secondary Containment Testing Report Form” to the local agency within 30 days of the completion of the secondary containment test. | 6 | 2660 | (d)
3 | 2637.1 | (e) | Owners or operators shall submit a copy of the “Spill Container Testing Report Form” to the local agency within 30 days of the completion of the spill container test. | 6 | 2660 | (d)
3 | 2637.2 | (e) | Owners or operators shall submit a copy of the “Overfill Prevention Equipment Inspection Report Form” to the local agency within 30 days of the completion of the overfill prevention equipment inspection. | 6 | 2660 | (d)
4 | 2644.1 | (a)(5) | Owners and operators of underground storage tanks subject to the requirements of this section shall submit a copy of the enhanced leak detection test report to the board and the local agency within 60 days of completion of the test. | 6 | 2660 | (d)
4 | 2643.1 | (0) | Tank Integrity Testing Requirements | 6 | 2662 |  | Tank Integrity Testing Requirements for Integrity Testing
3 | 2635 | (a)(5) | After installation, but before the underground storage tank is placed in service, a tank integrity test shall be conducted to ensure that no damage occurred during installation. The tank integrity test is not required if the tank is equipped with an interstitial monitor certified by a third party evaluator to meet the performance standards of a “tank integrity test” as defined in section 2611, or if the tank is tested using another method deemed by the State Water Resources Control Board to be equivalent. | 6 | 2662 | (b) | After installation, but before the underground storage tank is placed in service, a tank integrity test shall be conducted to ensure that no damage occurred during installation. The tank integrity test is not required if the tank is equipped with an interstitial monitor certified by a third party evaluator to meet the performance standards of a “tank integrity test” as defined in section 2611, or if the tank is tested using another method deemed by the State Water Resources Control Board to be equivalent. Integrity testing must be performed after installation, replacement, or repair of underground storage tank system primary containment components requiring excavation to access. Integrity testing must be performed prior to the system becoming operational:
|  |  |  | 6 | 2662 | (b)(1) | Standard Integrity Test – Type 1 underground storage tank are subject to integrity testing capable of detecting a liquid release of 0.1 gallon per hour from any portion of the underground storage tank system primary containment with a probability of detection of at least 95 percent and a probability of false alarm no greater than five percent.
4 | 2644.1 | (a)(2) | The enhanced leak detection test method shall be third party certified, in accordance with section 2643(f), for the capability of detecting both vapor and liquid phase releases from the underground storage tank system. The enhanced leak detection test method shall be capable of detecting a leak rate of at least 0.005 gallons per hour, with a probability of detection of at least 95 percent and a probability of false alarm no greater than five percent. | 6 | 2662 | (b)(2) | The enhanced leak detection test method shall be third party certified, in accordance with section 2643(f), for the capability Enhanced Leak Detection Test – Type 2 and Type 3 underground storage tanks are subject to integrity testing capable of detecting both vapor and liquid phase releases from the underground storage tank system. The enhanced leak detection test method shall be capable of detecting a leak rate of at least 0.005 gallons per hour from any portion of the underground storage tank system primary containment, with a probability of detection of at least 95 percent and a probability of false alarm no greater than five percent. The enhanced leak detection test cannot be performed until all ground penetrating work and surfacing has been completed.
3 | 2638 | (0) | Certification of Monitoring Equipment | 6 | 2663 |  | Requirements for Certification of Monitoring Release Detection Equipment Testing
3 | 2638 | (a) | All monitoring equipment used to satisfy the requirements of this article shall be installed, calibrated, operated and maintained in accordance with manufacturer’s instructions, and certified every 12 months for operability, proper operating condition, and proper calibration. Written records shall be maintained as required in section 2712. | 6 | 2663 | (a) | All monitoring Release detection equipment used to satisfy the requirements of this article shall must be installed, calibrated, operated and maintained tested in accordance with manufacturer’s instructions, and certified upon installation and at least once every 12 months for operability, proper operating condition, programming, and proper calibration by a service technician meeting the requirements of section 2633. Written records shall be maintained as required in section 2712. Testing of continuous vacuum, pressure, or hydrostatic interstitial release detection systems for piping must include verification of continuity to the extent practical as approved by the Unified Program Agency.
3 | 2638 | (b) | Persons performing installation, repair, maintenance, calibration, or certification of monitoring equipment shall meet the requirements set forth in section 2715(f). | 6 | 2663 | (a)
|  |  |  | 6 | 2663 | (c) | Testing of systems that utilize an impact shear valve to stop the flow of hazardous substance at the dispenser as part of the under-dispenser containment monitoring must verify proper function of mechanical release detection equipment and the impact shear valve to confirm that hazardous substance will not dispense when the impact shear valve is closed. If the impact shear valve does not completely shut off dispensing, or if a system of this type fails to function properly at any time, the valve and any other non-functional under-dispenser containment release detection equipment must be replaced in accordance with subparagraph 2652(a)(1)(B) prior to resuming dispensing from the dispenser monitored by the inoperable equipment.
|  |  |  | 6 | 2663 | (d) | Testing of line leak detectors that perform monitoring in accordance with section 2652(a)(3) as required by the facility’s monitoring program must be done by simulating a release equivalent to 0.1 gallon per hour defined at 150 percent of the normal operating pressure.
3 | 2638 | (c) | The monitoring equipment certification shall be made on a “Monitoring System Certification Form” located in Appendix VI. | 6 | 2663 | (e) | The monitoring equipment results of the release detection equipment certification shall test must be made recorded on a the "Monitoring System Certification Release Detection Equipment Testing Report Form" located in appendix VI 5.
3 | 2637.1 | (0) | Spill Container Testing | 6 | 2664 |  | Requirements for Spill Containment Container Testing
3 | 2637.1 | (a) | Spill containers shall be tested for tightness at all of the following times: | 6 | 2664 | (a) | Spill containers shall contaiment must be tested for tightness at all of the following times: upon installation, and at least once every 12 months by a service technician meeting the requirements of section 2633.
3 | 2637.1 | (a)(1) | Upon the completion of an installation and every 12 months thereafter; and | 6 | 2664 | (a)
3 | 2637.1 | (a)(2) | Within 30 days of the date of the completion of a repair. | 6 | 2664 | (a)
3 | 2637.1 | (c) | The spill container tests shall be performed by a service technician meeting the requirements of section 2715(f). | 6 | 2664 | (a)
3 | 2637.1 | (b) | The spill container tests shall be conducted using a testing procedure that demonstrates that the spill container is capable of containing the stored substance until it is detected and cleaned up. These tests shall be performed in accordance with manufacturer’s guidelines or standards. If there are no manufacturer’s guidelines or standards, the spill container shall be tested using an applicable method specified in an industry code or engineering standard. If there are no applicable manufacturer’s guidelines, industry codes, or engineering standards, a test method approved by a state registered professional engineer shall be used. | 6 | 2664 | (b) | The sSpill container containment tests shall must be conducted using a testing procedure that demonstrates that the spill container is capable of containment can containing the stored substance until it is detected and cleaned up. These tests shall must be performed in accordance with manufacturer’s guidelines or standards. If there are no manufacturer’s guidelines or standards, the spill container shall be tested using, an applicable method specified in an industry code or engineering standard. If there are no applicable manufacturer’s guidelines, industry codes, or engineering standards, a test method approved by a state registered professional engineer shall be used, or if approved by the Unified Program Agency, a test method developed by a state registered professional engineer shall be used.
|  |  |  | 6 | 2664 | (c) | The spill containment volume must be tested to confirm the liquid capacity is no less than five gallons.
3 | 2637.1 | (d) | The results of the spill container test shall be recorded on the “Spill Container Testing Report Form” located in Appendix VIII. | 6 | 2664 | (d) | The results of the spill container containment test shall must be recorded on the “Spill Container Containment Testing Report Form” located in appendix VIII 6.
3 | 2637.2 | (0) | Overfill Prevention Equipment Inspection | 6 | 2665 |  | Requirements for Overfill Prevention Equipment Inspection Testing
3 | 2637.2 | (d) | The results of the overfill prevention equipment inspection shall be recorded on the “Overfill Prevention Equipment Inspection Report Form” located in Appendix IX. | 6 | 2665 | (c) | The results of the overfill prevention equipment inspection shall test must be recorded on the “Overfill Prevention Equipment Inspection Testing Report Form” located in appendix IX 7.
3 | 2637 | (0) | Secondary Containment Testing | 6 | 2666 |  | Requirements for Secondary Containment Testing
3 | 2637 | (a)(1)(A) | Upon installation of a secondary containment system, six months after installation of a secondary containment system, and at least once every 36 months thereafter; | 6 | 2666 | (a) | Except as provided in subdivision (b), secondary containment must be tested for tightness Uupon installation of a secondary containment system, six months after installation of a secondary containment system, and at least once every 36 months thereafter by a service technician meeting the requirements of section 2633.
3 | 2637 | (a)(1)(B) | On and after October 1, 2018 all of the following times: | 6 | 2666 | (a) | On and after October 1, 2018 all of the following times:
3 | 2637 | (a)(1)(B)(i) | Within 30 days of the date of the completion of a repair to a secondary containment component; and | 6 | 2666 | (a)
3 | 2637 | (d) | Secondary containment tests shall be performed by a service technician meeting the requirements of section 2715(f). | 6 | 2666 | (a)
3 | 2637 | (a)(2) | Use a method of continuous monitoring that automatically monitors the integrity of both the primary and secondary containment such as components that are hydrostatically monitored or under constant vacuum or pressure. | 6 | 2666 | (b)(1) | Use a method of continuous monitoring that automatically monitors the integrity of both the primary and secondary containment such as components that are hydrostatically monitored or under constant vacuum or pressure. Secondary containment components monitored using continuous vacuum, pressure, or hydrostatic interstitial monitoring are exempt from periodic secondary containment testing requirements.
3 | 2637 | (a)(1)(B)(ii) | Within 30 days of the date of discontinuing the use of a method of continuous monitoring that automatically monitors the integrity of both the primary and secondary containment such as components that are hydrostatically monitored or under constant vacuum or pressure. | 6 | 2666 | (b)(2) | Secondary containment components of Type 1 and Type 2 underground storage tank systems must be tested Wwithin 30 days of the date of discontinuing the use of a method of continuous monitoring that automatically monitors the integrity of both vacuum, pressure, or hydrostatic interstitial monitoring of the primary and secondary containment such as components that are hydrostatically monitored or under constant vacuum or pressure system, and at least once every 36 months.
3 | 2637 | (c) | The testing of secondary containment systems shall be conducted using a test procedure that demonstrates that the system performs at least as well as it did upon installation. For example, if the secondary containment system was tested upon installation by using a test method that applied a pressure of five pounds per square inch, then the periodic test must be conducted using a method that tests the system at an equivalent pressure. These tests shall be performed in accordance with manufacturer’s guidelines or standards. If there are no manufacturer’s guidelines or standards, secondary containment systems must be tested using an applicable method specified in an industry code or engineering standard. If there are no applicable manufacturer’s guidelines, industry codes, or engineering standards, a test method approved by a state registered professional engineer shall be used. | 6 | 2666 | (c) | The tTesting of secondary containment systems shall must be conducted using a test procedure that demonstrates that the system performs at least as well as it did upon installation. For example, if the secondary containment system was tested upon installation by using a test method that applied a pressure of five pounds per square inch, then the periodic test must be conducted using a method that tests the system at an equivalent pressure. These tests shall must be performed in accordance with manufacturer’s guidelines, or standards. If there are no manufacturer’s guidelines or standards, secondary containment systems must be tested using an applicable method specified in an industry code or engineering standard,. If there are no applicable manufacturer’s guidelines, industry codes, or engineering standards, a test method approved or if approved by the Unified Program Agency, a test method developed by a state registered professional engineer shall be used.
3 | 2637 | (e) | On and after October 1, 2018, the results of the secondary containment test shall be recorded on the “Secondary Containment Testing Report Form” located in Appendix VII. | 6 | 2666 | (e) | On and after October 1, 2018, tThe results of the secondary containment test shall must be made recorded on the "Secondary Containment Testing Report Form" (located in Aappendix VII) 8.
5 | 0 | (0) | Release Reporting and Inititial Abatement Requirements | 7 | 0 |  | Unauthorized Release Reporting and Initial Abatement Response Requirements
5 | 2650 | (0) | Reporting and Recording Applicability | 7 | 2670 |  | Recording Requirements for Unauthorized Releases
5 | 2651 | (b) | The operator's monitoring records, as required under section 2712 of Article 10, shall include: | 7 | 2670 | (b) | The operator's monitoring records, as required under section 2712 of Article 10 2613(c), shall must include:
5 | 2651 | (c) | The integrity of the secondary containment shall be reviewed for possible deterioration under the following conditions: | 7 | 2670 | (c) | The integrity of the secondary containment shall must be reviewed for possible deterioration under the following conditions:
5 | 2651 | (c)(3) | Hazardous substances, other than those stored in the primary containment system, are added to the secondary containment to treat or neutralize the released hazardous substance and the added substance or resulting substance from such a combination is not compatible with the secondary containment. | 7 | 2670 | (c)(3) | Hazardous substances, other than those stored in the primary containment system, are added to the secondary containment to treat or neutralize the released hazardous substance and the added substance or resulting substance from such a combination is not compatible with the secondary containment.
5 | 2651 | (e) | Whenever the local agency reviews the operator's monitoring reports and finds that one or more recordable unauthorized releases have occurred, the local agency shall review the information included in the monitoring records pursuant to subsection (a), shall review the permit, and may inspect the underground storage tank pursuant to section 2712 (e) and (f) of Article 10. If the local agency finds that the containment and monitoring requirements of Articles 3 or 4 can no longer be met, the local agency shall require the owner or operator to cease operation of the underground storage tank system until appropriate modifications are made to comply with the requirements of Articles 3 or 4, as appropriate. | 7 | 2670 | (e) | Whenever the local agency Unified Program Agency reviews the operator's monitoring reports and finds that one or more recordable unauthorized releases have occurred, the local agency shall Unified Program Agency must review the information included in the monitoring records pursuant to subsection subdivision (a), shall review the permit, and may as necessary, inspect the underground storage tank pursuant to section 2712 (e) and (f) of Article 10, to determine if construction and monitoring requirements of article 4 or 5 still can be met . If the local agency Unified Program Agency finds that the containment construction and monitoring requirements of Aarticles 3 or 4 4 or 5 can no longer be met, the local agency shall Unified Program Agency must require the owner or operator to cease operation of the underground storage tank system until appropriate modifications are made to comply with the requirements of Aarticles 3 or 4 4 or 5, as appropriate.
5 | 2652 | (0) | Reporting, Investigation and Initial Response Requirements for Unauthorized Releases | 7 | 2671 |  | Reporting, Investigation, and Initial Response Requirements for Unauthorized Releases
5 | 2650 | (e) | The owner or operator of an underground storage tank shall report to the local agency any unauthorized release described in sections 25295 and 25295.5 of the Health and Safety Code, and shall also record and report any of the following conditions in accordance with section 2652: | 7 | 2671 | (a) | The owner or operator shall must record and provide a preliminary written report to the local agency Unified Program Agency for any unauthorized release that escapes from the secondary containment, any unauthorized release from the primary containment that is described in sections 25295 and 25295.5 of the Health and Safety Code, and shall also record and report any of the following conditions in accordance with this section 2652:
5 | 2650 | (e)(3) |  | 7 | 2671 | (a)(3)(B) | The owner or operator is not required to submit a preliminary report to the Unified Program Agency if the condition described in subparagraph (A) system equipment is found determined to be the result of defective but has equipment, the condition did not leaked, and result in an unauthorized release, the defective equipment is immediately repaired or replaced, and any liquid in the interstitial space not used as part of the interstitial release detection method is immediately removed.
5 | 2650 | (e)(4) | (1) Monitoring results from a release detection method required under Article 3 or Article 4 that indicate a release may have occurred, unless the monitoring device is found to be defective, and is immediately repaired, recalibrated or replaced, and additional monitoring does not confirm the initial results. | 7 | 2671 | (a)(4) | Monitoring results from a release detection method required under Article 3 or Aarticle 4 5 that indicate an unauthorized release may have occurred, unless the monitoring device release detection equipment is found to be defective, and the defective equipment is immediately repaired, recalibrated, or replaced, and additional monitoring does not confirm the initial results.
5 | 2652 | (c) | Within five working days of detecting an unauthorized release, the owner or operator shall submit to the local agency through the California Environmental Reporting System or a local reporting portal a full written report which shall include, but not be limited to, all of the following information to the extent that the information is known at the time of filing the report: | 7 | 2671 | (c) | Within five working days of detecting a reportable unauthorized release, the owner or operator shall submit must provide to the local agency Unified Program Agency through the California Environmental Reporting System or a local reporting portal a full preliminary written report, which shall include including, but not be limited to, all of the following information to the extent that the information is known at the time of filing the preliminary written report:
|  |  |  | 7 | 2671 | (c)(02) | Facility address and the CERS ID Number;
7 | 0 | (0) | Undergound Storage Tank Closure Requirements | 8 | 0 |  | Underground Storage Tank Closure Requirements
7 | 2671 | (0) | Temporary Closure Requirements | 8 | 2680 |  | Temporary Closure Requirements
7 | 2671 | (a) | An owner or operator shall comply with all of the following requirements to complete and maintain temporary closure of an underground storage tank: | 8 | 2680 | (f) | An The owner or operator shall must comply with all of the following requirements to complete and maintain qualify for temporary closure of an underground storage tank:
7 | 2671 | (a)(1) | All residual liquid, solids, or sludges shall be removed and handled in accordance with the applicable provisions of Chapters 6.5 and 6.7 of Division 20 of the Health and Safety Code. | 8 | 2680 | (f)(1) | All residual liquid, solids, or and sludges shall must be removed and handled in accordance with the applicable provisions of Cchapters 6.5 and 6.7 of Ddivision 20 of the Health and Safety Code.
7 | 2671 | (d) | At the end of a temporary closure period over 12 months, including any extension granted by the local agency, the owner may reuse the underground storage tank only if the tank meets the requirements of Article 3 for new underground storage tanks or is upgraded to meet the requirements of Article 6. | 8 | 2680 | (i) | At the end of a temporary closure period over 12 months, including any extension granted by the local agency, the owner or operator may reuse put the underground storage tank system back into operation only if the tank it meets the requirements of Article 3 for new underground storage tanks or is upgraded to meet the requirements of chapter 6.7 of division 20 of the Health and Safety Code and the construction, monitoring, and testing requirements of Aarticles 4, 5, and 6.
|  |  |  | 8 | 2680 | (j) | The owner or operator must update all applicable data elements in the California Environmental Reporting System or local reporting portal within 30 days of the beginning and the end of the temporary closure period in accordance with section 2613(b).
7 | 2672 | (0) | Permanent Closure Requirements | 8 | 2681 |  | Permanent Closure Requirements
7 | 2670 | (f) | At least 30 calendar days prior to closure, or within a shorter period of time approved by the local agency, the owner or operator who intends to close a tank shall submit to the local agency for approval, a proposal for compliance with section 2671 or 2672, as appropriate. | 8 | 2681 | (a) | At least 30 calendar days prior to closure, or within a shorter period of time if directed as permitted by the local agency Unified Program Agency, the an owner or operator who intends to permanently close an underground storage tank system shall submit must provide to the local agency Unified Program Agency for approval a proposal for compliance with this section 2671 or 2672, as appropriate. During the period of time between cessation of hazardous substance storage and completion of underground storage tank permanent closure pursuant to in accordance with this section 2671 or 2672, the applicable containment construction and monitoring requirements of Aarticles 3 or 4 shall 4 and 5 continue to apply. The time between cessation of hazardous substance storage and application for permanent closure must not exceed 90 days. Closure must be completed within a reasonable time as determined by the local agency Unified Program Agency, but not to exceed 365 days from the date of approval by the Unified Program Agency.
7 | 2670 | (e) | During the period of time between cessation of hazardous substance storage and actual completion of underground storage tank closure pursuant to section 2671 or 2672, the applicable containment and monitoring requirements of Articles 3 or 4 shall continue to apply. The time period between cessation of hazardous substance storage and application for temporary or permanent tank closure shall not exceed 90 calendar days. Closure shall be completed within a reasonable time period as determined by the local agency. | 8 | 2681 | (a)
7 | 2672 | (a) | Owners or operators of underground storage tanks subject to permanent closure shall comply with either subdivision (b) below for underground storage tank removal or subdivision (c) below for closure in place. It is not essential that all portions of an underground storage tank be permanently closed in the same manner; however, all closure actions shall be conducted in accordance with this section. Subdivisions (d) and (e) below apply to all underground storage tanks subject to permanent closure. | 8 | 2681 | (c) | For all portions of the underground storage tank, the Oowners or operators of an underground storage tanks system subject to permanent closure shall must comply with either subdivision (b) below (e) for underground storage tank removal or subdivision (c) below (f) for closure in place. It is not essential that all portions of an underground storage tank system be permanently closed in the same manner; however, all closure actions shall must be conducted in accordance with this section. Subdivisions (d) and (e) below apply to all underground storage tanks subject to permanent closure.
7 | 2672 | (b) | Owners or operators of underground storage tanks subject to permanent closure shall comply with applicable provisions of Chapter 6.5 of Division 20 of the Health and Safety Code and with the following requirements: | 8 | 2681 | (e) | The Oowners or operators of an underground storage tanks system subject to permanent closure shall must comply with applicable provisions of Cchapter 6.5 of Ddivision 20 of the Health and Safety Code and with the following requirements:
7 | 2672 | (b)(1) | All residual liquid, solids, or sludges shall be removed and handled as hazardous wastes or recyclable materials in accordance with Chapter 6.5 of the Health and Safety Code. | 8 | 2681 | (e)(1) | All residual liquid, solids, or and sludges shall must be removed and handled as hazardous wastes or recyclable materials in accordance with Chapter 6.5 of the Health and Safety Code.
7 | 2672 | (c) | Owners or operators of underground storage tanks subject to permanent closure where the tanks are approved to be closed in place shall comply with the applicable provisions of Chapters 6.5 and 6.7 of Division 20 of the Health and Safety Code and with the following requirements: | 8 | 2681 | (f) | The Oowners or operators of an underground storage tanks system subject to permanent closure where the tanks are approved to be closed closure in place must comply with the applicable provisions of Cchapters 6.5 and 6.7 of Ddivision 20 of the Health and Safety Code and with the following requirements:
7 | 2672 | (c)(1) | All residual liquid, solids, or sludges shall be removed and handled as a hazardous waste or recyclable materials in accordance with Chapters 6.5 and 6.7 of the Health and Safety Code. | 8 | 2681 | (f)(1) | All residual liquid, solids, or and sludges shall must be removed and handled as a hazardous waste or recyclable materials in accordance with Chapters 6.5 and 6.7 of the Health and Safety Code.
7 | 2672 | (d) | The owner or operator of an underground storage tank being closed pursuant to this section shall demonstrate to the satisfaction of the local agency that an unauthorized release has not occurred. This demonstration shall be based on soil sample analysis and/or water analysis if water is present in the excavation. This analysis shall be performed during or immediately after closure activities. If the demonstration is based on soil sample analysis, soil samples shall be taken and analyzed as follows: | 8 | 2681 | (g) | The owner or operator of an underground storage tank system being permanently closed pursuant to this section shall demonstrate to the satisfaction of the local agency that an unauthorized release has not occurred. This demonstration shall be based on must perform soil sample analysis, and/or water analysis if water is present in the excavation, groundwater analysis. This analysis shall be performed during or immediately after closure activities. If the demonstration is based on soil sample analysis, soil samples shall be taken and analyzed Sampling must be performed as follows:
7 | 2672 | (d)(1) | If the underground storage tank or any portion thereof is removed, soil samples shall be taken immediately beneath the removed portions of the tank, a minimum of two feet into native material at each end of the tank in accordance with section 2649. A separate sample shall be taken for each 20 linear-feet of trench for piping. | 8 | 2681 | (g)(1) | If the underground storage tank or any portion thereof is removed, sSoil and groundwater samples must be analyzed as required by the Cleanup Oversight Agency for all hazardous substances previously stored in the underground storage tank(s). Soil samples shall must be taken immediately beneath the removed portions of the tank, collected a minimum of two feet into native material at each end of the tank in accordance with section 2649. A separate sample shall be taken for each 20 linear-feet of trench for piping. soil, immediately beneath:
7 | 2672 | (d)(1) |  | 8 | 2681 | (g)(1)(A) | immediately beneath the removed portions Each end of the tank, a minimum of two feet into native material at each end of the tank in accordance with section 2649. An additional sample must be collected at the midpoint of each tank with a capacity greater than 12,000 gallons. Compartmented tanks require an additional sample taken beneath each internal bulkhead, to be analyzed in accordance with subdivision (h) as required for all hazardous substances previously stored in both tanks as required by the Cleanup Oversight Agency.
|  |  |  | 8 | 2681 | (g)(1)(B) | The midpoint of each tank with a capacity greater than 12,000 gallons;
|  |  |  | 8 | 2681 | (g)(1)(C) | Each internal bulkhead of compartmented tanks;
7 | 2672 | (d)(1) |  | 8 | 2681 | (g)(1)(D) | A separate sample shall taken for each All hazardous substance piping at 20 linear-feet of trench for piping. foot intervals, with additional samples collected at each change in direction for rigid piping; and
7 | 2672 | (d)(1) |  | 8 | 2681 | (g)(1)(E) | Each dispenser.
|  |  |  | 8 | 2681 | (g)(2) | Soil sample collection must be performed immediately after removal of the tank or hazardous substance piping from the excavation. Groundwater sample collection must be done immediately after the water enters the excavation or is otherwise encountered.
|  |  |  | 8 | 2681 | (i) | Within 30 days of removal of the tank or piping, or collection of required soil or groundwater samples, the owner or operator must provide to the Unified Program Agency:
|  |  |  | 8 | 2681 | (i)(4) | Documentation demonstrating proper disposal of the tank, pipe, and any hazardous wastes generated as a result of closure activities.
|  |  |  | 8 | 2681 | (k) | Within 60 days of receipt of all the documentation in subdivision (i) and the submittal pursuant to subdivision (n), the Unified Program Agency must issue an Underground Storage Tank Closure Letter to the owner or operator that confirms that the underground storage tank system has been permanently closed in accordance with this section and includes all the following:
|  |  |  | 8 | 2681 | (n) | The owner or operator must update all applicable data elements in the California Environmental Reporting System or local reporting portal within 30 days of removal of the underground storage tank from the excavation or, for closure in place, certification of the tank as non-hazardous after on-site cleaning, in accordance with section 2613(b).
|  |  |  | 8 | 2682 |  | Abandoned Underground Storage Tanks
|  |  |  | 8 | 2682 | (b) | Abandoned underground storage tanks must be inspected annually by the Unified Program Agency in accordance with section 25288 of the Health and Safety Code and the Unified Program Agency’s Inspection and Enforcement Plan.
|  |  |  | 8 | 2683 |  | Underground Storage Tank Reuse and Reinstallation Requirements
|  |  |  | 8 | 2683 | (a) | An underground storage tank intended to be reused to store a non-hazardous substance, or to be moved from its current location to be reused for any purpose, must be permanently closed in accordance with section 2681 prior to being moved or reused, if approved by the Unified Program Agency. The owner or operator must provide the following information to the Unified Program Agency, within the timeframe specified by that agency:
|  |  |  | 8 | 2683 | (a)(1) | The name(s) of the new owner and new operator, if applicable;
|  |  |  | 8 | 2683 | (a)(2) | The location of intended use;
|  |  |  | 8 | 2683 | (a)(3) | The nature of intended use; and
|  |  |  | 8 | 2683 | (a)(4) | Approval from the Unified Program Agency where the underground storage tank will be reinstalled.
7 | 2672 | (b)(4) | An owner or operator of an underground storage tank or any part thereof that is destined for a specific reuse shall advise the local agency, within the time frame specified by that agency, of: | 8 | 2683 | (a)
7 | 2672 | (b)(4)(A) | The name of the new owner and new operator of the underground storage tank; | 8 | 2683 | (a)(1)
7 | 2672 | (b)(4)(B) | The location of intended use; and | 8 | 2683 | (a)(2)
7 | 2672 | (b)(4)(C) | The nature of intended use. | 8 | 2683 | (a)(3)
|  |  |  | 8 | 2683 | (b) | If a tank will be reused to store a hazardous substance, an underground storage tank that has been relocated must be tested, inspected, and certified by the manufacturer and by an independent testing organization no more than 30 days before reinstallation and meet the requirements of section 25290.1 of the Health and Safety Code, and articles 4, 5, and 6, before reuse. The independent testing organization label must be updated to include both the original manufacture date and the recertification date.
|  |  |  | 8 | 2684 |  | Cleanup Oversight Agency Notification and Review
|  |  |  | 8 | 2684 | (a) | Within 30 days of receipt of the closure documentation specified in section 2681(i), the Unified Program Agency must submit to the Cleanup Oversight Agency all the following:
|  |  |  | 8 | 2684 | (a)(11) | Date, location at the facility, and depth of samples collected;
|  |  |  | 8 | 2684 | (c) | If the Cleanup Oversight Agency determines that no further investigation or corrective action is required, the Cleanup Oversight Agency must notify the owner, operator, and property owner in writing that all actions necessary to demonstrate compliance with section 2681 and section 25298 of the Health and Safety Code have been taken, that no further investigation or corrective actions are required, and that the underground storage tank is closed pursuant to section 2681.
10 | 0 | (0) | Permit Application, Quarterly Report, and Trade Secret Request Requirements | 9 | 0 |  | Permit Application, Unified Program Agency Requirements, Trade Secrets Request, and Red Tag Requirements
10 | 2711 | (0) | Information and Application for Permit to Operate an Underground Storage Tank | 9 | 2690 |  | Information and Operating Permit Applications for Permit to Operate an Underground Storage Tanks
10 | 2711 | (a) | The permit application shall include, but not be limited to, the following information to the extent such information is known to the permit applicant: | 9 | 2690 | (a) | An application for an operating permit must be submitted to the Unified Program Agency by the owner or operator. The permit application shall must include, but not be limited to, the following information, to the extent such information is known to the permit applicant:
10 | 2711 | (a)(2) | The name, location, mailing address, and telephone number where the underground storage tank is located, and type of business involved, if any. | 9 | 2690 | (a)(2) | Facility Information — The name, California Department of Tax and Fee Administration number, location, mailing address, and telephone number of the facility where the underground storage tank is located, and type of business involved, if any.
10 | 2711 | (a)(11) | Documentation to show compliance with state and federal financial responsibility requirements applicable to underground storage tanks containing petroleum. | 9 | 2690 | (a)(5) | Financial Responsibility Mechanisms — Documentation to show Identification of mechanisms used to demonstrate compliance with state and federal financial responsibility requirements applicable to for petroleum underground storage tanks containing petroleum as specified in sections 25292.2 and 25299.31 of the Health and Safety Code, the federal act, and regulations adopted pursuant to the federal act, or specify that the facility is exempt from the requirements. If required to demonstrate financial responsibility, the owner or operator must submit a current Certification of Financial Responsibility and maintain all applicable supporting mechanisms available for review by the Unified Program Agency or the Board upon request, or as otherwise required by the Federal Act.
10 | 2712 | (0) | Permit Conditions | 9 | 2691 |  | Operating Permit Conditions
2 | 2620 | (b) | Owners and operators shall comply with these regulations except as otherwise specifically provided herein. If the operator is not the owner, then the owner shall enter into a written contract with the operator requiring the operator to monitor the underground storage tank; maintain appropriate records; and implement reporting procedures as required by any applicable permit. Both the owner and operator are responsible for assuring that the underground storage tank system is repaired or upgraded in accordance with Article 6, or closed in accordance with Article 7, as appropriate. | 9 | 2691 | (a) | Owners and operators shall comply with these regulations except as otherwise specifically provided herein. If the operator owner is not the owner operator, then the owner shall must enter into a written contract agreement with the operator requiring the operator to monitor the underground storage tank; maintain appropriate records; and implement reporting procedures as required by any applicable ensure the underground storage tank system is in compliance with chapter 6.7 of division 20 of the Health and Safety Code, this chapter, and the operating permit. Both the owner and operator are responsible for assuring that the underground storage tank system is repaired or upgraded in accordance with Article 6, or closed in accordance with Article 7, as appropriate.
2 | 2620 | (c) | The owner of a farm or heating oil tank or any tank which is exempt from regulation as an underground storage tank by virtue of its use shall, prior to any change which results in the tank becoming subject to regulation, obtain a valid operating permit. | 9 | 2691 | (f) | The owner of of a farm or heating oil tank or any tank which is exempt from regulation as an underground storage tank by virtue of its use shall, prior to any change which results in the tank becoming subject to regulation, An owner or operator of a tank that is excluded or exempt from this chapter pursuant to section 2612 must obtain a valid operating permit and comply with section 25290.1 of the Health and Safety Code before any change in tank use or other condition occurs that results in the tank losing its exclusion or exemption.
10 | 2713 | (0) | Local Agency Reporting Requirements | 9 | 2692 |  | Local Unified Program Agency Reporting Requirements
10 | 2713 | (c) | On a semi-annual basis, each local agency shall send to the Board, information pertaining to local underground storage tank program implementation and enforcement activities. This information shall be submitted using a local information management system, local reporting portal, or the California Environmental Reporting System, and shall include, but not be limited to the number of: | 9 | 2692 | (a) | On a semi-annual basis, each local agency shall Unified Program Agency must send to the Board, information pertaining to local underground storage tank program implementation and enforcement activities. This information must be submitted using the California Environmental Reporting System, and shall must include, but not be limited to, the number of:
10 | 2713 | (c)(4) | Inspected facilities in compliance with release detection, spill prevention, overfill prevention, corrosion protection, financial responsibility, and designated operator training and inspection requirements | 9 | 2692 | (a)(4) | Inspected facilities in compliance with all applicable release detection, spill prevention, overfill prevention, corrosion protection, financial responsibility, and designated operator training and inspection requirements, and financial responsibility; and
10 | 2713 | (d)(2) | The report shall include the following California Environmental Reporting System items: CERSID, Facility Name, UST Reporting Requirement, UST Last Inspection Date, and written explanation why the compliance inspection was not performed. | 9 | 2692 | (b)(2) | The report shall must include the following California Environmental Reporting System items: CERS ID, Facility Name, UST Reporting Requirement, UST Last Inspection Date, and written explanation why the compliance inspection was not performed.
10 | 2713 | (d)(2) |  | 9 | 2692 | (b)(2)(A) | CERS ID,;
10 | 2713 | (d)(2) |  | 9 | 2692 | (b)(2)(B) | Facility Name,;
10 | 2713 | (d)(2) |  | 9 | 2692 | (b)(2)(C) | UST Reporting Requirement,;
10 | 2713 | (d)(2) |  | 9 | 2692 | (b)(2)(D) | UST Last Inspection Date,; and
10 | 2713 | (d)(2) |  | 9 | 2692 | (b)(2)(E) | wWritten explanation why the compliance inspection was not performed.
10.5 | 2717.1 | (0) | Affixing Red Tags | 9 | 2694 |  | Affixing Enforcement, Violation Classification, and Red Tags Application
10 | 2712 | (g) | The local agency shall take appropriate enforcement action pursuant to section 25299 of the Health and Safety Code or prohibit the operation of the tank systems if the owner or operator fails to comply with the monitoring requirements in Article 3 or 4 or the reporting requirements of Article 5. | 9 | 2694 | (a) | The local agency shall take appropriate enforcement action pursuant to section 25299 of the Health and Safety Code or prohibit the operation of the tank systems if the owner or operator fails to comply with the monitoring requirements in Article 3 or 4 or the reporting requirements of Article 5. To promote the effective detection, abatement, and deterrence of violations, the Unified Program Agency and the Board must initiate enforcement actions against owners and operators of noncompliant underground storage tank systems consistent with an Inspection and Enforcement Plan developed and implemented consistent with this section.
|  |  |  | 9 | 2694 | (a)(1) | Each Inspection and Enforcement Plan must include procedures for the following:
|  |  |  | 9 | 2694 | (a)(1)(B) | Verifying and documenting return to compliance based on information provided or submitted by or on behalf of the owner or operator, by conducting follow-up inspections, or by a combination of those methods; and
10 | 2712 | (g) | The local agency shall take appropriate enforcement action pursuant to section 25299 of the Health and Safety Code or prohibit the operation of the tank systems if the owner or operator fails to comply with the monitoring requirements in Article 3 or 4 or the reporting requirements of Article 5. | 9 | 2694 | (b) | The local agency shall Unified Program Agency and the Board must take appropriate enforcement action pursuant to section 25299 of the Health and Safety Code or prohibit the operation of the an underground storage tank systems if the owner or operator fails to comply with the construction, monitoring, testing, and reporting requirements in Article 3 or 4 or the reporting requirements of A of articles 4, 5, 6, and 7.
|  |  |  | 9 | 2694 | (c) | When performing any underground storage tank inspection, the Unified Program Agency or the Board must classify each violation cited as minor, Class II, or Class I, pursuant to this chapter and consistent with the applicable Inspection and Enforcement Plan.
10.5 | 2717.1 | (a) | Upon the discovery of a significant violation that poses an imminent threat to human health or safety or the environment, the local agency may immediately affix a red tag to the fill pipe of the non-compliant underground storage tank system using a tamper-resistant strap or straps, fill pipe bag, or any combination thereof so that the tag is visible to any person attempting to deliver petroleum to the underground storage tank. Immediately after affixing a red tag pursuant to this subdivision, the local agency shall notify the operator, if present on site, of the significant violation(s) for which the red tag was issued. Within 24 hours of affixing a red tag pursuant to this subdivision, the local agency shall notify the owner of the significant violation(s) for which the red tag was issued. | 9 | 2694 | (d) | Upon the discovery of a If the Unified Program Agency or the Board determines that an underground storage tank system is in significant violation that and poses an imminent threat to human health or safety or the environment, the local agency Unified Program Agency or the Board may immediately affix a red tag to the fill pipe of the non-compliant underground storage tank system using a tamper-resistant strap or straps, fill pipe bag, or any combination thereof so that the tag is visible to any person attempting to deliver petroleum, deposit, or input a hazardous substance into, or withdraw a hazardous substance from, the underground storage tank. Immediately after affixing a red tag pursuant to this subdivision, the local agency shall notify the operator, if present on site, of the significant violation(s) for which the red tag was issued. Within 24 hours of affixing a red tag pursuant to this subdivision, the local agency shall notify the owner of the significant violation(s) for which the red tag was issued.
|  |  |  | 9 | 2694 | (f) | The Unified Program Agency or the Board has the authority to direct the owner or operator to empty an underground storage tank to which a red tag has been affixed within a timeframe determined by the Unified Program Agency or the Board, as applicable, not to exceed 48 hours from when the red tag is affixed. The underground storage tank system must not be emptied through the dispenser.
10.5 | 2717.1 | (c) | Before affixing a red tag to the fill pipe of an underground storage tank system, the local agency shall document the level of stored product in the tank. | 9 | 2694 | (h) | Before affixing a red tag to the fill pipe of an underground storage tank system, tThe local agency shall Unified Program Agency or the Board must document the level of stored product hazardous substance in the tank. immediately before:
10.5 | 2717.1 | (c) |  | 9 | 2694 | (h)(1) | Affixing a red tag to the fill pipe of an underground storage tank; and
|  |  |  | 9 | 2694 | (h)(2) | Emptying of a red tagged tank as ordered by the Unified Program Agency or the Board.
10.5 | 2717.1 | (a) |  | 9 | 2694 | (i) | Immediately aAfter affixing a red tag pursuant to this subdivision, the local agency Board or the Unified Program Agency, whichever affixed the red tag, shall must notify the owner and operator in writing, immediately if present on site, or within 24 hours if not on site, of the significant violation(s) for which the red tag was issued. Within 24 hours of affixing a red tag pursuant to this subdivision, the local agency shall notify the owner of the significant violation(s) for which the red tag was issued.
10.5 | 2717.1 | (f) | No person may deposit petroleum into an underground storage tank system that has a red tag affixed to its fill pipe. | 9 | 2694 | (j) | No person may deposit petroleum An owner or operator must not allow the delivery, depositing, or inputting of a hazardous substance into, or withdrawal of hazardous substance from, an underground storage tank system that has a red tag affixed to its fill pipe without written authorization from the Board or the Unified Program Agency, whichever affixed the red tag.
10.5 | 2717.1 | (e) | No owner or operator of a facility may deposit or allow the deposit of petroleum into an underground storage tank system that has a red tag affixed to the system's fill pipe. | 9 | 2694 | (j)
|  |  |  | 9 | 2694 | (l) | If the Board affixed the red tag, the Board may request that the Unified Program Agency perform any required inspections and authorization duties in accordance with section 2695(c).
|  |  |  | 9 | 2694 | (m) | If a red tag is removed to facilitate the emptying of a non-compliant underground storage tank or facilitate necessary repairs, the Unified Program Agency or the Board must reaffix the red tag to the fill pipe of the tank immediately after the tank is emptied or if the repairs are complete and the tank remains in significant violation.
10.5 | 2717.4 |  | Upon making a determination that a significant violation has been corrected, the local agency shall notify the owner or operator in writing of its determination. | 9 | 2694 | (n) | Upon making a determination that a significant violation has been corrected to the satisfaction of the Board or the Unified Program Agency, whichever affixed the red tag, the local agency Board or the Unified Program Agency shall must notify the owner or operator in writing of its determination.
10.5 | 2717.2 | (0) | Removing Red Tags | 9 | 2695 |  | Removing Removal of Red Tags
10.5 | 2717.2 | (a) | Upon notification by the owner or operator documenting to the satisfaction of the local agency that the significant violation has been corrected, the local agency may provide written authorization to the owner or operator to remove the red tag. The local agency shall inspect the underground storage tank system within five business days of notification to determine whether the system continues to be in significant violation, regardless of whether it has authorized removal of the red tag by the owner or operator. If, upon inspection, the local agency determines that the system is no longer in significant violation and it has not already authorized removal of the red tag, the local agency shall immediately remove the red tag. | 9 | 2695 | (b) | If, upon inspection, the local agency Board or the Unified Program Agency, whichever affixed the red tag, determines that the system is no longer in significant violation and it has not already authorized removal of the red tag, the local agency Board or the Unified Program Agency that affixed the red tag shall must immediately remove the red tag.
10.5 | 2717.2 | (a) |  | 9 | 2695 | (c) | Upon notification by the owner or operator documenting, to the satisfaction of the local agency Board or the Unified Program Agency, whichever affixed the red tag, that the significant violation has been corrected, the local agency Board or Unified Program Agency may provide written authorization to the owner or operator to remove the red tag. The local agency Board or the Unified Program Agency shall must inspect the underground storage tank system within five business days of notification to determine whether the system continues to be in significant violation, regardless of whether it the Board or the Unified Program Agency has authorized removal of the red tag by the owner or operator.
10.5 | 2717.2 | (b) | Upon removing a red tag from an underground storage tank system, the local agency shall document the level of stored product in the tank. If the owner or operator removes a red tag pursuant to written authorization by the local agency, the owner or operator shall document the level of stored product in the tank immediately after removing the red tag. | 9 | 2695 | (d) | Upon removing a red tag from an underground storage tank system, the local agency Board or the Unified Program Agency must shall document the level of stored product in the tank. If the owner or operator removes a red tag pursuant to written authorization by the local agency Board or the Unified Program Agency, the owner or operator shall must document the level of stored product hazardous substance in the tank immediately after removing the red tag.
10.5 | 2717.2 | (c) | A red tag that has been removed by the owner or operator shall be returned to the local agency within five business days, or sooner if requested by the local agency. | 9 | 2695 | (f) | A red tag that has been removed by the owner or operator shall must be returned to the local agency Board or the Unified Program Agency, whichever affixed the red tag, within five business days, or sooner if requested by the local agency. The owner or operator must provide documentation of the level of stored hazardous substance in accordance with subdivision (d) when returning the red tag.
10.5 | 2717.5 | (0) | Content of Red Tags | 9 | 2696 |  | Content of Red Tags
10.5 | 2717.5 | (b) | Red tags shall bear the following information on both sides of the tag: | 9 | 2696 | (b) | Red tags must bear the following information on both sides of the tag:
10.5 | 2717.5 | (b)(2) | The following wording, printed in white below the wording described in subdivision (b)(1) in at least 16 point type: “Delivering petroleum, or removing, defacing, altering, or otherwise tampering with this tag may result in civil penalties of up to $5000 per day.” | 9 | 2696 | (b)(2) | The following wording, printed in white below the wording described in subdivision (b) paragraph (1) in at least 16-point type: “Delivering petroleum, or removing, defacing, altering, or otherwise tampering with this tag withdrawing any hazardous substance may result in civil penalties liability of up to $5,000 per day per UST.”
10.5 | 2717.5 | (b)(4) | Following the wording described in subdivision (b)(3), there shall be a blank area at least 1/2 inch wide by three inches long in which the local agency shall write legibly in permanent ink its name and telephone number. | 9 | 2696 | (b)(4) | Following the wording described in subdivision paragraph (b)(3), there shall must be a blank area at least 1/2 inch wide by three inches long in which the local agency Board or the Unified Program Agency, whichever affixed the red tag, shall must write legibly in permanent ink its name and telephone number.
10.5 | 2717.5 | (b)(6) | In the lower right hand corner, a graphic comprised of a blue background, the letters SWRCB in black, and white wavy lines depicting water. | 9 | 2696 | (b)(6) | In the lower right-hand corner, a graphic comprised of a blue background, the letters "SWRCB" in black, and white wavy lines depicting water.
11 | 0 | (0) | Corrective Action Requirements | 10 | 0 |  | Corrective Action and Post-Closure Abatement Requirements
|  |  |  | 10 | 2709 |  | Oversight Authority
|  |  |  | 10 | 2709 |  | Only Cleanup Oversight Agencies have authority to oversee the abatement of unauthorized releases of hazardous substances from underground storage tanks, including corrective action and post-closure abatement.
11 | 2722 | (0) | Scope of Corrective Action | 10 | 2710 |  | Scope of Corrective Action
|  |  |  | 10 | 2710 | (a) | A responsible party must take corrective action in compliance with the following requirements:
|  |  |  | 10 | 2710 | (a)(1) | All applicable waste discharge requirements or other orders issued pursuant to division 7, commencing with section 13000, of the Water Code;
5 | 2655 | (0) | Free Product Removal Requirements | 10 | 2712 |  | Free Product Removal Requirements
5 | 2655 | (a) | At sites where investigations made pursuant to section 2652 indicate the presence of free product, the owner or operator shall comply with the requirements of this section. The owner or operator shall remove free product to the maximum extent practicable, as determined by the local agency, while continuing to take any actions required under sections 2652 through 2654. | 10 | 2712 | (a) | At sites where investigations made pursuant to section 2652 2671 indicate the presence of free product, the owner or operator shall a responsible party must comply with the requirements of this section. The owner or operator shall A responsible party must remove free product to the maximum extent practicable, as determined by the local agency, Cleanup Oversight Agency while continuing to take any actions required under sections 2652 through 2654.
5 | 2655 | (e) | A free product removal report shall be submitted through GeoTracker to the agency overseeing the cleanup within 45 calendar days of release confirmation and shall include, but not be limited to: | 10 | 2712 | (e) | A responsible party must submit to the Cleanup Oversight Agency Aa free product removal report shall be submitted through GeoTracker to the agency overseeing the cleanup within 45 calendar days of release confirmation and shall include, but not be limited to, including at a minimum:
5 | 2655 | (e)(4) | Whether any discharge will take place on-site or off-site during the recovery operation and, if so, where this discharge will be located; | 10 | 2712 | (e)(4) | Whether any discharge will take place on- site or off- site during the recovery operation and, if so, where this discharge will be located;
|  |  |  | 10 | 2714 |  | Corrective Action Plan Development Phase
11 | 2726 | (0) | Corrective Action Plan Implementation Phase | 10 | 2715 |  | Corrective Action Plan Implementation Phase
11 | 2727 | (0) | Verification Monitoring Phase | 10 | 2716 |  | Verification Monitoring Phase
|  |  |  | 10 | 2717 |  | Closure Preparation Phase
|  |  |  | 10 | 2718 |  | Closure Denial Petitions and Closure Reviews
|  |  |  | 10 | 2719 |  | Closure
|  |  |  | 10 | 2720 |  | Post-Closure Abatement
11 | 2728 | (0) | Public Participation | 10 | 2721 |  | Public Participation